## StudyCase
Case | LF_Method | Tolerance | Iteration limit | Initialization | System Freq | Earth Resistivity | Load | Reference bus | VoltageStart | Source Voltage BFS | AngleRef | Load Voltage Sentivity factor | LoadData
1 | 0 | 0.0001 | 500 | 0 | 50 | 100 | 0 | 1000 | 1 | 0 | 0 | 0.75 | 0
Note on E1: hemanth: 0 - Flat Start 1 - Pre defined
Note on G1: Author: earth sentivity for computing the line impedance using carson's eq
Note on K1: 0- voltage data reference from db 1- voltage data from online data
Note on N1: Author: 0 - from db 1 - from real time feed (Not available for public)

## Nodes
BusNo | BusName | ZoneNo | Vnom (kVLL) | Vmin | Vmax
1 | Bus1 | 1 | 0.416 | 0.3744 | 0.4576
2 | Bus2 | 1 | 0.416 | 0.3744 | 0.4576
3 | Bus3 | 1 | 0.416 | 0.3744 | 0.4576
4 | Bus4 | 1 | 0.416 | 0.3744 | 0.4576
5 | Bus5 | 1 | 0.416 | 0.3744 | 0.4576
6 | Bus6 | 1 | 0.416 | 0.3744 | 0.4576
7 | Bus7 | 1 | 0.416 | 0.3744 | 0.4576
8 | Bus8 | 1 | 0.416 | 0.3744 | 0.4576
9 | Bus9 | 1 | 0.416 | 0.3744 | 0.4576
10 | Bus10 | 1 | 0.416 | 0.3744 | 0.4576
11 | Bus11 | 1 | 0.416 | 0.3744 | 0.4576
12 | Bus12 | 1 | 0.416 | 0.3744 | 0.4576
13 | Bus13 | 1 | 0.416 | 0.3744 | 0.4576
14 | Bus14 | 1 | 0.416 | 0.3744 | 0.4576
15 | Bus15 | 1 | 0.416 | 0.3744 | 0.4576
16 | Bus16 | 1 | 0.416 | 0.3744 | 0.4576
17 | Bus17 | 1 | 0.416 | 0.3744 | 0.4576
18 | Bus18 | 1 | 0.416 | 0.3744 | 0.4576
19 | Bus19 | 1 | 0.416 | 0.3744 | 0.4576
20 | Bus20 | 1 | 0.416 | 0.3744 | 0.4576
21 | Bus21 | 1 | 0.416 | 0.3744 | 0.4576
22 | Bus22 | 1 | 0.416 | 0.3744 | 0.4576
23 | Bus23 | 1 | 0.416 | 0.3744 | 0.4576
24 | Bus24 | 1 | 0.416 | 0.3744 | 0.4576
25 | Bus25 | 1 | 0.416 | 0.3744 | 0.4576
26 | Bus26 | 1 | 0.416 | 0.3744 | 0.4576
27 | Bus27 | 1 | 0.416 | 0.3744 | 0.4576
28 | Bus28 | 1 | 0.416 | 0.3744 | 0.4576
29 | Bus29 | 1 | 0.416 | 0.3744 | 0.4576
30 | Bus30 | 1 | 0.416 | 0.3744 | 0.4576
31 | Bus31 | 1 | 0.416 | 0.3744 | 0.4576
32 | Bus32 | 1 | 0.416 | 0.3744 | 0.4576
33 | Bus33 | 1 | 0.416 | 0.3744 | 0.4576
34 | Bus34 | 1 | 0.416 | 0.3744 | 0.4576
35 | Bus35 | 1 | 0.416 | 0.3744 | 0.4576
36 | Bus36 | 1 | 0.416 | 0.3744 | 0.4576
37 | Bus37 | 1 | 0.416 | 0.3744 | 0.4576
38 | Bus38 | 1 | 0.416 | 0.3744 | 0.4576
39 | Bus39 | 1 | 0.416 | 0.3744 | 0.4576
40 | Bus40 | 1 | 0.416 | 0.3744 | 0.4576
41 | Bus41 | 1 | 0.416 | 0.3744 | 0.4576
42 | Bus42 | 1 | 0.416 | 0.3744 | 0.4576
43 | Bus43 | 1 | 0.416 | 0.3744 | 0.4576
44 | Bus44 | 1 | 0.416 | 0.3744 | 0.4576
45 | Bus45 | 1 | 0.416 | 0.3744 | 0.4576
46 | Bus46 | 1 | 0.416 | 0.3744 | 0.4576
47 | Bus47 | 1 | 0.416 | 0.3744 | 0.4576
48 | Bus48 | 1 | 0.416 | 0.3744 | 0.4576
49 | Bus49 | 1 | 0.416 | 0.3744 | 0.4576
50 | Bus50 | 1 | 0.416 | 0.3744 | 0.4576
51 | Bus51 | 1 | 0.416 | 0.3744 | 0.4576
52 | Bus52 | 1 | 0.416 | 0.3744 | 0.4576
53 | Bus53 | 1 | 0.416 | 0.3744 | 0.4576
54 | Bus54 | 1 | 0.416 | 0.3744 | 0.4576
55 | Bus55 | 1 | 0.416 | 0.3744 | 0.4576
56 | Bus56 | 1 | 0.416 | 0.3744 | 0.4576
57 | Bus57 | 1 | 0.416 | 0.3744 | 0.4576
58 | Bus58 | 1 | 0.416 | 0.3744 | 0.4576
59 | Bus59 | 1 | 0.416 | 0.3744 | 0.4576
60 | Bus60 | 1 | 0.416 | 0.3744 | 0.4576
61 | Bus61 | 1 | 0.416 | 0.3744 | 0.4576
62 | Bus62 | 1 | 0.416 | 0.3744 | 0.4576
63 | Bus63 | 1 | 0.416 | 0.3744 | 0.4576
64 | Bus64 | 1 | 0.416 | 0.3744 | 0.4576
65 | Bus65 | 1 | 0.416 | 0.3744 | 0.4576
66 | Bus66 | 1 | 0.416 | 0.3744 | 0.4576
67 | Bus67 | 1 | 0.416 | 0.3744 | 0.4576
68 | Bus68 | 1 | 0.416 | 0.3744 | 0.4576
69 | Bus69 | 1 | 0.416 | 0.3744 | 0.4576
70 | Bus70 | 1 | 0.416 | 0.3744 | 0.4576
71 | Bus71 | 1 | 0.416 | 0.3744 | 0.4576
72 | Bus72 | 1 | 0.416 | 0.3744 | 0.4576
73 | Bus73 | 1 | 0.416 | 0.3744 | 0.4576
74 | Bus74 | 1 | 0.416 | 0.3744 | 0.4576
75 | Bus75 | 1 | 0.416 | 0.3744 | 0.4576
76 | Bus76 | 1 | 0.416 | 0.3744 | 0.4576
77 | Bus77 | 1 | 0.416 | 0.3744 | 0.4576
78 | Bus78 | 1 | 0.416 | 0.3744 | 0.4576
79 | Bus79 | 1 | 0.416 | 0.3744 | 0.4576
80 | Bus80 | 1 | 0.416 | 0.3744 | 0.4576
81 | Bus81 | 1 | 0.416 | 0.3744 | 0.4576
82 | Bus82 | 1 | 0.416 | 0.3744 | 0.4576
83 | Bus83 | 1 | 0.416 | 0.3744 | 0.4576
84 | Bus84 | 1 | 0.416 | 0.3744 | 0.4576
85 | Bus85 | 1 | 0.416 | 0.3744 | 0.4576
86 | Bus86 | 1 | 0.416 | 0.3744 | 0.4576
87 | Bus87 | 1 | 0.416 | 0.3744 | 0.4576
88 | Bus88 | 1 | 0.416 | 0.3744 | 0.4576
89 | Bus89 | 1 | 0.416 | 0.3744 | 0.4576
90 | Bus90 | 1 | 0.416 | 0.3744 | 0.4576
91 | Bus91 | 1 | 0.416 | 0.3744 | 0.4576
92 | Bus92 | 1 | 0.416 | 0.3744 | 0.4576
93 | Bus93 | 1 | 0.416 | 0.3744 | 0.4576
94 | Bus94 | 1 | 0.416 | 0.3744 | 0.4576
95 | Bus95 | 1 | 0.416 | 0.3744 | 0.4576
96 | Bus96 | 1 | 0.416 | 0.3744 | 0.4576
97 | Bus97 | 1 | 0.416 | 0.3744 | 0.4576
98 | Bus98 | 1 | 0.416 | 0.3744 | 0.4576
99 | Bus99 | 1 | 0.416 | 0.3744 | 0.4576
100 | Bus100 | 1 | 0.416 | 0.3744 | 0.4576
101 | Bus101 | 1 | 0.416 | 0.3744 | 0.4576
102 | Bus102 | 1 | 0.416 | 0.3744 | 0.4576
103 | Bus103 | 1 | 0.416 | 0.3744 | 0.4576
104 | Bus104 | 1 | 0.416 | 0.3744 | 0.4576
105 | Bus105 | 1 | 0.416 | 0.3744 | 0.4576
106 | Bus106 | 1 | 0.416 | 0.3744 | 0.4576
107 | Bus107 | 1 | 0.416 | 0.3744 | 0.4576
108 | Bus108 | 1 | 0.416 | 0.3744 | 0.4576
109 | Bus109 | 1 | 0.416 | 0.3744 | 0.4576
110 | Bus110 | 1 | 0.416 | 0.3744 | 0.4576
111 | Bus111 | 1 | 0.416 | 0.3744 | 0.4576
112 | Bus112 | 1 | 0.416 | 0.3744 | 0.4576
113 | Bus113 | 1 | 0.416 | 0.3744 | 0.4576
114 | Bus114 | 1 | 0.416 | 0.3744 | 0.4576
115 | Bus115 | 1 | 0.416 | 0.3744 | 0.4576
116 | Bus116 | 1 | 0.416 | 0.3744 | 0.4576
117 | Bus117 | 1 | 0.416 | 0.3744 | 0.4576
118 | Bus118 | 1 | 0.416 | 0.3744 | 0.4576
119 | Bus119 | 1 | 0.416 | 0.3744 | 0.4576
120 | Bus120 | 1 | 0.416 | 0.3744 | 0.4576
121 | Bus121 | 1 | 0.416 | 0.3744 | 0.4576
122 | Bus122 | 1 | 0.416 | 0.3744 | 0.4576
123 | Bus123 | 1 | 0.416 | 0.3744 | 0.4576
124 | Bus124 | 1 | 0.416 | 0.3744 | 0.4576
125 | Bus125 | 1 | 0.416 | 0.3744 | 0.4576
126 | Bus126 | 1 | 0.416 | 0.3744 | 0.4576
127 | Bus127 | 1 | 0.416 | 0.3744 | 0.4576
128 | Bus128 | 1 | 0.416 | 0.3744 | 0.4576
129 | Bus129 | 1 | 0.416 | 0.3744 | 0.4576
130 | Bus130 | 1 | 0.416 | 0.3744 | 0.4576
131 | Bus131 | 1 | 0.416 | 0.3744 | 0.4576
132 | Bus132 | 1 | 0.416 | 0.3744 | 0.4576
133 | Bus133 | 1 | 0.416 | 0.3744 | 0.4576
134 | Bus134 | 1 | 0.416 | 0.3744 | 0.4576
135 | Bus135 | 1 | 0.416 | 0.3744 | 0.4576
136 | Bus136 | 1 | 0.416 | 0.3744 | 0.4576
137 | Bus137 | 1 | 0.416 | 0.3744 | 0.4576
138 | Bus138 | 1 | 0.416 | 0.3744 | 0.4576
139 | Bus139 | 1 | 0.416 | 0.3744 | 0.4576
140 | Bus140 | 1 | 0.416 | 0.3744 | 0.4576
141 | Bus141 | 1 | 0.416 | 0.3744 | 0.4576
142 | Bus142 | 1 | 0.416 | 0.3744 | 0.4576
143 | Bus143 | 1 | 0.416 | 0.3744 | 0.4576
144 | Bus144 | 1 | 0.416 | 0.3744 | 0.4576
145 | Bus145 | 1 | 0.416 | 0.3744 | 0.4576
146 | Bus146 | 1 | 0.416 | 0.3744 | 0.4576
147 | Bus147 | 1 | 0.416 | 0.3744 | 0.4576
148 | Bus148 | 1 | 0.416 | 0.3744 | 0.4576
149 | Bus149 | 1 | 0.416 | 0.3744 | 0.4576
150 | Bus150 | 1 | 0.416 | 0.3744 | 0.4576
151 | Bus151 | 1 | 0.416 | 0.3744 | 0.4576
152 | Bus152 | 1 | 0.416 | 0.3744 | 0.4576
153 | Bus153 | 1 | 0.416 | 0.3744 | 0.4576
154 | Bus154 | 1 | 0.416 | 0.3744 | 0.4576
155 | Bus155 | 1 | 0.416 | 0.3744 | 0.4576
156 | Bus156 | 1 | 0.416 | 0.3744 | 0.4576
157 | Bus157 | 1 | 0.416 | 0.3744 | 0.4576
158 | Bus158 | 1 | 0.416 | 0.3744 | 0.4576
159 | Bus159 | 1 | 0.416 | 0.3744 | 0.4576
160 | Bus160 | 1 | 0.416 | 0.3744 | 0.4576
161 | Bus161 | 1 | 0.416 | 0.3744 | 0.4576
162 | Bus162 | 1 | 0.416 | 0.3744 | 0.4576
163 | Bus163 | 1 | 0.416 | 0.3744 | 0.4576
164 | Bus164 | 1 | 0.416 | 0.3744 | 0.4576
165 | Bus165 | 1 | 0.416 | 0.3744 | 0.4576
166 | Bus166 | 1 | 0.416 | 0.3744 | 0.4576
167 | Bus167 | 1 | 0.416 | 0.3744 | 0.4576
168 | Bus168 | 1 | 0.416 | 0.3744 | 0.4576
169 | Bus169 | 1 | 0.416 | 0.3744 | 0.4576
170 | Bus170 | 1 | 0.416 | 0.3744 | 0.4576
171 | Bus171 | 1 | 0.416 | 0.3744 | 0.4576
172 | Bus172 | 1 | 0.416 | 0.3744 | 0.4576
173 | Bus173 | 1 | 0.416 | 0.3744 | 0.4576
174 | Bus174 | 1 | 0.416 | 0.3744 | 0.4576
175 | Bus175 | 1 | 0.416 | 0.3744 | 0.4576
176 | Bus176 | 1 | 0.416 | 0.3744 | 0.4576
177 | Bus177 | 1 | 0.416 | 0.3744 | 0.4576
178 | Bus178 | 1 | 0.416 | 0.3744 | 0.4576
179 | Bus179 | 1 | 0.416 | 0.3744 | 0.4576
180 | Bus180 | 1 | 0.416 | 0.3744 | 0.4576
181 | Bus181 | 1 | 0.416 | 0.3744 | 0.4576
182 | Bus182 | 1 | 0.416 | 0.3744 | 0.4576
183 | Bus183 | 1 | 0.416 | 0.3744 | 0.4576
184 | Bus184 | 1 | 0.416 | 0.3744 | 0.4576
185 | Bus185 | 1 | 0.416 | 0.3744 | 0.4576
186 | Bus186 | 1 | 0.416 | 0.3744 | 0.4576
187 | Bus187 | 1 | 0.416 | 0.3744 | 0.4576
188 | Bus188 | 1 | 0.416 | 0.3744 | 0.4576
189 | Bus189 | 1 | 0.416 | 0.3744 | 0.4576
190 | Bus190 | 1 | 0.416 | 0.3744 | 0.4576
191 | Bus191 | 1 | 0.416 | 0.3744 | 0.4576
192 | Bus192 | 1 | 0.416 | 0.3744 | 0.4576
193 | Bus193 | 1 | 0.416 | 0.3744 | 0.4576
194 | Bus194 | 1 | 0.416 | 0.3744 | 0.4576
195 | Bus195 | 1 | 0.416 | 0.3744 | 0.4576
196 | Bus196 | 1 | 0.416 | 0.3744 | 0.4576
197 | Bus197 | 1 | 0.416 | 0.3744 | 0.4576
198 | Bus198 | 1 | 0.416 | 0.3744 | 0.4576
199 | Bus199 | 1 | 0.416 | 0.3744 | 0.4576
200 | Bus200 | 1 | 0.416 | 0.3744 | 0.4576
201 | Bus201 | 1 | 0.416 | 0.3744 | 0.4576
202 | Bus202 | 1 | 0.416 | 0.3744 | 0.4576
203 | Bus203 | 1 | 0.416 | 0.3744 | 0.4576
204 | Bus204 | 1 | 0.416 | 0.3744 | 0.4576
205 | Bus205 | 1 | 0.416 | 0.3744 | 0.4576
206 | Bus206 | 1 | 0.416 | 0.3744 | 0.4576
207 | Bus207 | 1 | 0.416 | 0.3744 | 0.4576
208 | Bus208 | 1 | 0.416 | 0.3744 | 0.4576
209 | Bus209 | 1 | 0.416 | 0.3744 | 0.4576
210 | Bus210 | 1 | 0.416 | 0.3744 | 0.4576
211 | Bus211 | 1 | 0.416 | 0.3744 | 0.4576
212 | Bus212 | 1 | 0.416 | 0.3744 | 0.4576
213 | Bus213 | 1 | 0.416 | 0.3744 | 0.4576
214 | Bus214 | 1 | 0.416 | 0.3744 | 0.4576
215 | Bus215 | 1 | 0.416 | 0.3744 | 0.4576
216 | Bus216 | 1 | 0.416 | 0.3744 | 0.4576
217 | Bus217 | 1 | 0.416 | 0.3744 | 0.4576
218 | Bus218 | 1 | 0.416 | 0.3744 | 0.4576
219 | Bus219 | 1 | 0.416 | 0.3744 | 0.4576
220 | Bus220 | 1 | 0.416 | 0.3744 | 0.4576
221 | Bus221 | 1 | 0.416 | 0.3744 | 0.4576
222 | Bus222 | 1 | 0.416 | 0.3744 | 0.4576
223 | Bus223 | 1 | 0.416 | 0.3744 | 0.4576
224 | Bus224 | 1 | 0.416 | 0.3744 | 0.4576
225 | Bus225 | 1 | 0.416 | 0.3744 | 0.4576
226 | Bus226 | 1 | 0.416 | 0.3744 | 0.4576
227 | Bus227 | 1 | 0.416 | 0.3744 | 0.4576
228 | Bus228 | 1 | 0.416 | 0.3744 | 0.4576
229 | Bus229 | 1 | 0.416 | 0.3744 | 0.4576
230 | Bus230 | 1 | 0.416 | 0.3744 | 0.4576
231 | Bus231 | 1 | 0.416 | 0.3744 | 0.4576
232 | Bus232 | 1 | 0.416 | 0.3744 | 0.4576
233 | Bus233 | 1 | 0.416 | 0.3744 | 0.4576
234 | Bus234 | 1 | 0.416 | 0.3744 | 0.4576
235 | Bus235 | 1 | 0.416 | 0.3744 | 0.4576
236 | Bus236 | 1 | 0.416 | 0.3744 | 0.4576
237 | Bus237 | 1 | 0.416 | 0.3744 | 0.4576
238 | Bus238 | 1 | 0.416 | 0.3744 | 0.4576
239 | Bus239 | 1 | 0.416 | 0.3744 | 0.4576
240 | Bus240 | 1 | 0.416 | 0.3744 | 0.4576
241 | Bus241 | 1 | 0.416 | 0.3744 | 0.4576
242 | Bus242 | 1 | 0.416 | 0.3744 | 0.4576
243 | Bus243 | 1 | 0.416 | 0.3744 | 0.4576
244 | Bus244 | 1 | 0.416 | 0.3744 | 0.4576
245 | Bus245 | 1 | 0.416 | 0.3744 | 0.4576
246 | Bus246 | 1 | 0.416 | 0.3744 | 0.4576
247 | Bus247 | 1 | 0.416 | 0.3744 | 0.4576
248 | Bus248 | 1 | 0.416 | 0.3744 | 0.4576
249 | Bus249 | 1 | 0.416 | 0.3744 | 0.4576
250 | Bus250 | 1 | 0.416 | 0.3744 | 0.4576
251 | Bus251 | 1 | 0.416 | 0.3744 | 0.4576
252 | Bus252 | 1 | 0.416 | 0.3744 | 0.4576
253 | Bus253 | 1 | 0.416 | 0.3744 | 0.4576
254 | Bus254 | 1 | 0.416 | 0.3744 | 0.4576
255 | Bus255 | 1 | 0.416 | 0.3744 | 0.4576
256 | Bus256 | 1 | 0.416 | 0.3744 | 0.4576
257 | Bus257 | 1 | 0.416 | 0.3744 | 0.4576
258 | Bus258 | 1 | 0.416 | 0.3744 | 0.4576
259 | Bus259 | 1 | 0.416 | 0.3744 | 0.4576
260 | Bus260 | 1 | 0.416 | 0.3744 | 0.4576
261 | Bus261 | 1 | 0.416 | 0.3744 | 0.4576
262 | Bus262 | 1 | 0.416 | 0.3744 | 0.4576
263 | Bus263 | 1 | 0.416 | 0.3744 | 0.4576
264 | Bus264 | 1 | 0.416 | 0.3744 | 0.4576
265 | Bus265 | 1 | 0.416 | 0.3744 | 0.4576
266 | Bus266 | 1 | 0.416 | 0.3744 | 0.4576
267 | Bus267 | 1 | 0.416 | 0.3744 | 0.4576
268 | Bus268 | 1 | 0.416 | 0.3744 | 0.4576
269 | Bus269 | 1 | 0.416 | 0.3744 | 0.4576
270 | Bus270 | 1 | 0.416 | 0.3744 | 0.4576
271 | Bus271 | 1 | 0.416 | 0.3744 | 0.4576
272 | Bus272 | 1 | 0.416 | 0.3744 | 0.4576
273 | Bus273 | 1 | 0.416 | 0.3744 | 0.4576
274 | Bus274 | 1 | 0.416 | 0.3744 | 0.4576
275 | Bus275 | 1 | 0.416 | 0.3744 | 0.4576
276 | Bus276 | 1 | 0.416 | 0.3744 | 0.4576
277 | Bus277 | 1 | 0.416 | 0.3744 | 0.4576
278 | Bus278 | 1 | 0.416 | 0.3744 | 0.4576
279 | Bus279 | 1 | 0.416 | 0.3744 | 0.4576
280 | Bus280 | 1 | 0.416 | 0.3744 | 0.4576
281 | Bus281 | 1 | 0.416 | 0.3744 | 0.4576
282 | Bus282 | 1 | 0.416 | 0.3744 | 0.4576
283 | Bus283 | 1 | 0.416 | 0.3744 | 0.4576
284 | Bus284 | 1 | 0.416 | 0.3744 | 0.4576
285 | Bus285 | 1 | 0.416 | 0.3744 | 0.4576
286 | Bus286 | 1 | 0.416 | 0.3744 | 0.4576
287 | Bus287 | 1 | 0.416 | 0.3744 | 0.4576
288 | Bus288 | 1 | 0.416 | 0.3744 | 0.4576
289 | Bus289 | 1 | 0.416 | 0.3744 | 0.4576
290 | Bus290 | 1 | 0.416 | 0.3744 | 0.4576
291 | Bus291 | 1 | 0.416 | 0.3744 | 0.4576
292 | Bus292 | 1 | 0.416 | 0.3744 | 0.4576
293 | Bus293 | 1 | 0.416 | 0.3744 | 0.4576
294 | Bus294 | 1 | 0.416 | 0.3744 | 0.4576
295 | Bus295 | 1 | 0.416 | 0.3744 | 0.4576
296 | Bus296 | 1 | 0.416 | 0.3744 | 0.4576
297 | Bus297 | 1 | 0.416 | 0.3744 | 0.4576
298 | Bus298 | 1 | 0.416 | 0.3744 | 0.4576
299 | Bus299 | 1 | 0.416 | 0.3744 | 0.4576
300 | Bus300 | 1 | 0.416 | 0.3744 | 0.4576
301 | Bus301 | 1 | 0.416 | 0.3744 | 0.4576
302 | Bus302 | 1 | 0.416 | 0.3744 | 0.4576
303 | Bus303 | 1 | 0.416 | 0.3744 | 0.4576
304 | Bus304 | 1 | 0.416 | 0.3744 | 0.4576
305 | Bus305 | 1 | 0.416 | 0.3744 | 0.4576
306 | Bus306 | 1 | 0.416 | 0.3744 | 0.4576
307 | Bus307 | 1 | 0.416 | 0.3744 | 0.4576
308 | Bus308 | 1 | 0.416 | 0.3744 | 0.4576
309 | Bus309 | 1 | 0.416 | 0.3744 | 0.4576
310 | Bus310 | 1 | 0.416 | 0.3744 | 0.4576
311 | Bus311 | 1 | 0.416 | 0.3744 | 0.4576
312 | Bus312 | 1 | 0.416 | 0.3744 | 0.4576
313 | Bus313 | 1 | 0.416 | 0.3744 | 0.4576
314 | Bus314 | 1 | 0.416 | 0.3744 | 0.4576
315 | Bus315 | 1 | 0.416 | 0.3744 | 0.4576
316 | Bus316 | 1 | 0.416 | 0.3744 | 0.4576
317 | Bus317 | 1 | 0.416 | 0.3744 | 0.4576
318 | Bus318 | 1 | 0.416 | 0.3744 | 0.4576
319 | Bus319 | 1 | 0.416 | 0.3744 | 0.4576
320 | Bus320 | 1 | 0.416 | 0.3744 | 0.4576
321 | Bus321 | 1 | 0.416 | 0.3744 | 0.4576
322 | Bus322 | 1 | 0.416 | 0.3744 | 0.4576
323 | Bus323 | 1 | 0.416 | 0.3744 | 0.4576
324 | Bus324 | 1 | 0.416 | 0.3744 | 0.4576
325 | Bus325 | 1 | 0.416 | 0.3744 | 0.4576
326 | Bus326 | 1 | 0.416 | 0.3744 | 0.4576
327 | Bus327 | 1 | 0.416 | 0.3744 | 0.4576
328 | Bus328 | 1 | 0.416 | 0.3744 | 0.4576
329 | Bus329 | 1 | 0.416 | 0.3744 | 0.4576
330 | Bus330 | 1 | 0.416 | 0.3744 | 0.4576
331 | Bus331 | 1 | 0.416 | 0.3744 | 0.4576
332 | Bus332 | 1 | 0.416 | 0.3744 | 0.4576
333 | Bus333 | 1 | 0.416 | 0.3744 | 0.4576
334 | Bus334 | 1 | 0.416 | 0.3744 | 0.4576
335 | Bus335 | 1 | 0.416 | 0.3744 | 0.4576
336 | Bus336 | 1 | 0.416 | 0.3744 | 0.4576
337 | Bus337 | 1 | 0.416 | 0.3744 | 0.4576
338 | Bus338 | 1 | 0.416 | 0.3744 | 0.4576
339 | Bus339 | 1 | 0.416 | 0.3744 | 0.4576
340 | Bus340 | 1 | 0.416 | 0.3744 | 0.4576
341 | Bus341 | 1 | 0.416 | 0.3744 | 0.4576
342 | Bus342 | 1 | 0.416 | 0.3744 | 0.4576
343 | Bus343 | 1 | 0.416 | 0.3744 | 0.4576
344 | Bus344 | 1 | 0.416 | 0.3744 | 0.4576
345 | Bus345 | 1 | 0.416 | 0.3744 | 0.4576
346 | Bus346 | 1 | 0.416 | 0.3744 | 0.4576
347 | Bus347 | 1 | 0.416 | 0.3744 | 0.4576
348 | Bus348 | 1 | 0.416 | 0.3744 | 0.4576
349 | Bus349 | 1 | 0.416 | 0.3744 | 0.4576
350 | Bus350 | 1 | 0.416 | 0.3744 | 0.4576
351 | Bus351 | 1 | 0.416 | 0.3744 | 0.4576
352 | Bus352 | 1 | 0.416 | 0.3744 | 0.4576
353 | Bus353 | 1 | 0.416 | 0.3744 | 0.4576
354 | Bus354 | 1 | 0.416 | 0.3744 | 0.4576
355 | Bus355 | 1 | 0.416 | 0.3744 | 0.4576
356 | Bus356 | 1 | 0.416 | 0.3744 | 0.4576
357 | Bus357 | 1 | 0.416 | 0.3744 | 0.4576
358 | Bus358 | 1 | 0.416 | 0.3744 | 0.4576
359 | Bus359 | 1 | 0.416 | 0.3744 | 0.4576
360 | Bus360 | 1 | 0.416 | 0.3744 | 0.4576
361 | Bus361 | 1 | 0.416 | 0.3744 | 0.4576
362 | Bus362 | 1 | 0.416 | 0.3744 | 0.4576
363 | Bus363 | 1 | 0.416 | 0.3744 | 0.4576
364 | Bus364 | 1 | 0.416 | 0.3744 | 0.4576
365 | Bus365 | 1 | 0.416 | 0.3744 | 0.4576
366 | Bus366 | 1 | 0.416 | 0.3744 | 0.4576
367 | Bus367 | 1 | 0.416 | 0.3744 | 0.4576
368 | Bus368 | 1 | 0.416 | 0.3744 | 0.4576
369 | Bus369 | 1 | 0.416 | 0.3744 | 0.4576
370 | Bus370 | 1 | 0.416 | 0.3744 | 0.4576
371 | Bus371 | 1 | 0.416 | 0.3744 | 0.4576
372 | Bus372 | 1 | 0.416 | 0.3744 | 0.4576
373 | Bus373 | 1 | 0.416 | 0.3744 | 0.4576
374 | Bus374 | 1 | 0.416 | 0.3744 | 0.4576
375 | Bus375 | 1 | 0.416 | 0.3744 | 0.4576
376 | Bus376 | 1 | 0.416 | 0.3744 | 0.4576
377 | Bus377 | 1 | 0.416 | 0.3744 | 0.4576
378 | Bus378 | 1 | 0.416 | 0.3744 | 0.4576
379 | Bus379 | 1 | 0.416 | 0.3744 | 0.4576
380 | Bus380 | 1 | 0.416 | 0.3744 | 0.4576
381 | Bus381 | 1 | 0.416 | 0.3744 | 0.4576
382 | Bus382 | 1 | 0.416 | 0.3744 | 0.4576
383 | Bus383 | 1 | 0.416 | 0.3744 | 0.4576
384 | Bus384 | 1 | 0.416 | 0.3744 | 0.4576
385 | Bus385 | 1 | 0.416 | 0.3744 | 0.4576
386 | Bus386 | 1 | 0.416 | 0.3744 | 0.4576
387 | Bus387 | 1 | 0.416 | 0.3744 | 0.4576
388 | Bus388 | 1 | 0.416 | 0.3744 | 0.4576
389 | Bus389 | 1 | 0.416 | 0.3744 | 0.4576
390 | Bus390 | 1 | 0.416 | 0.3744 | 0.4576
391 | Bus391 | 1 | 0.416 | 0.3744 | 0.4576
392 | Bus392 | 1 | 0.416 | 0.3744 | 0.4576
393 | Bus393 | 1 | 0.416 | 0.3744 | 0.4576
394 | Bus394 | 1 | 0.416 | 0.3744 | 0.4576
395 | Bus395 | 1 | 0.416 | 0.3744 | 0.4576
396 | Bus396 | 1 | 0.416 | 0.3744 | 0.4576
397 | Bus397 | 1 | 0.416 | 0.3744 | 0.4576
398 | Bus398 | 1 | 0.416 | 0.3744 | 0.4576
399 | Bus399 | 1 | 0.416 | 0.3744 | 0.4576
400 | Bus400 | 1 | 0.416 | 0.3744 | 0.4576
401 | Bus401 | 1 | 0.416 | 0.3744 | 0.4576
402 | Bus402 | 1 | 0.416 | 0.3744 | 0.4576
403 | Bus403 | 1 | 0.416 | 0.3744 | 0.4576
404 | Bus404 | 1 | 0.416 | 0.3744 | 0.4576
405 | Bus405 | 1 | 0.416 | 0.3744 | 0.4576
406 | Bus406 | 1 | 0.416 | 0.3744 | 0.4576
407 | Bus407 | 1 | 0.416 | 0.3744 | 0.4576
408 | Bus408 | 1 | 0.416 | 0.3744 | 0.4576
409 | Bus409 | 1 | 0.416 | 0.3744 | 0.4576
410 | Bus410 | 1 | 0.416 | 0.3744 | 0.4576
411 | Bus411 | 1 | 0.416 | 0.3744 | 0.4576
412 | Bus412 | 1 | 0.416 | 0.3744 | 0.4576
413 | Bus413 | 1 | 0.416 | 0.3744 | 0.4576
414 | Bus414 | 1 | 0.416 | 0.3744 | 0.4576
415 | Bus415 | 1 | 0.416 | 0.3744 | 0.4576
416 | Bus416 | 1 | 0.416 | 0.3744 | 0.4576
417 | Bus417 | 1 | 0.416 | 0.3744 | 0.4576
418 | Bus418 | 1 | 0.416 | 0.3744 | 0.4576
419 | Bus419 | 1 | 0.416 | 0.3744 | 0.4576
420 | Bus420 | 1 | 0.416 | 0.3744 | 0.4576
421 | Bus421 | 1 | 0.416 | 0.3744 | 0.4576
422 | Bus422 | 1 | 0.416 | 0.3744 | 0.4576
423 | Bus423 | 1 | 0.416 | 0.3744 | 0.4576
424 | Bus424 | 1 | 0.416 | 0.3744 | 0.4576
425 | Bus425 | 1 | 0.416 | 0.3744 | 0.4576
426 | Bus426 | 1 | 0.416 | 0.3744 | 0.4576
427 | Bus427 | 1 | 0.416 | 0.3744 | 0.4576
428 | Bus428 | 1 | 0.416 | 0.3744 | 0.4576
429 | Bus429 | 1 | 0.416 | 0.3744 | 0.4576
430 | Bus430 | 1 | 0.416 | 0.3744 | 0.4576
431 | Bus431 | 1 | 0.416 | 0.3744 | 0.4576
432 | Bus432 | 1 | 0.416 | 0.3744 | 0.4576
433 | Bus433 | 1 | 0.416 | 0.3744 | 0.4576
434 | Bus434 | 1 | 0.416 | 0.3744 | 0.4576
435 | Bus435 | 1 | 0.416 | 0.3744 | 0.4576
436 | Bus436 | 1 | 0.416 | 0.3744 | 0.4576
437 | Bus437 | 1 | 0.416 | 0.3744 | 0.4576
438 | Bus438 | 1 | 0.416 | 0.3744 | 0.4576
439 | Bus439 | 1 | 0.416 | 0.3744 | 0.4576
440 | Bus440 | 1 | 0.416 | 0.3744 | 0.4576
441 | Bus441 | 1 | 0.416 | 0.3744 | 0.4576
442 | Bus442 | 1 | 0.416 | 0.3744 | 0.4576
443 | Bus443 | 1 | 0.416 | 0.3744 | 0.4576
444 | Bus444 | 1 | 0.416 | 0.3744 | 0.4576
445 | Bus445 | 1 | 0.416 | 0.3744 | 0.4576
446 | Bus446 | 1 | 0.416 | 0.3744 | 0.4576
447 | Bus447 | 1 | 0.416 | 0.3744 | 0.4576
448 | Bus448 | 1 | 0.416 | 0.3744 | 0.4576
449 | Bus449 | 1 | 0.416 | 0.3744 | 0.4576
450 | Bus450 | 1 | 0.416 | 0.3744 | 0.4576
451 | Bus451 | 1 | 0.416 | 0.3744 | 0.4576
452 | Bus452 | 1 | 0.416 | 0.3744 | 0.4576
453 | Bus453 | 1 | 0.416 | 0.3744 | 0.4576
454 | Bus454 | 1 | 0.416 | 0.3744 | 0.4576
455 | Bus455 | 1 | 0.416 | 0.3744 | 0.4576
456 | Bus456 | 1 | 0.416 | 0.3744 | 0.4576
457 | Bus457 | 1 | 0.416 | 0.3744 | 0.4576
458 | Bus458 | 1 | 0.416 | 0.3744 | 0.4576
459 | Bus459 | 1 | 0.416 | 0.3744 | 0.4576
460 | Bus460 | 1 | 0.416 | 0.3744 | 0.4576
461 | Bus461 | 1 | 0.416 | 0.3744 | 0.4576
462 | Bus462 | 1 | 0.416 | 0.3744 | 0.4576
463 | Bus463 | 1 | 0.416 | 0.3744 | 0.4576
464 | Bus464 | 1 | 0.416 | 0.3744 | 0.4576
465 | Bus465 | 1 | 0.416 | 0.3744 | 0.4576
466 | Bus466 | 1 | 0.416 | 0.3744 | 0.4576
467 | Bus467 | 1 | 0.416 | 0.3744 | 0.4576
468 | Bus468 | 1 | 0.416 | 0.3744 | 0.4576
469 | Bus469 | 1 | 0.416 | 0.3744 | 0.4576
470 | Bus470 | 1 | 0.416 | 0.3744 | 0.4576
471 | Bus471 | 1 | 0.416 | 0.3744 | 0.4576
472 | Bus472 | 1 | 0.416 | 0.3744 | 0.4576
473 | Bus473 | 1 | 0.416 | 0.3744 | 0.4576
474 | Bus474 | 1 | 0.416 | 0.3744 | 0.4576
475 | Bus475 | 1 | 0.416 | 0.3744 | 0.4576
476 | Bus476 | 1 | 0.416 | 0.3744 | 0.4576
477 | Bus477 | 1 | 0.416 | 0.3744 | 0.4576
478 | Bus478 | 1 | 0.416 | 0.3744 | 0.4576
479 | Bus479 | 1 | 0.416 | 0.3744 | 0.4576
480 | Bus480 | 1 | 0.416 | 0.3744 | 0.4576
481 | Bus481 | 1 | 0.416 | 0.3744 | 0.4576
482 | Bus482 | 1 | 0.416 | 0.3744 | 0.4576
483 | Bus483 | 1 | 0.416 | 0.3744 | 0.4576
484 | Bus484 | 1 | 0.416 | 0.3744 | 0.4576
485 | Bus485 | 1 | 0.416 | 0.3744 | 0.4576
486 | Bus486 | 1 | 0.416 | 0.3744 | 0.4576
487 | Bus487 | 1 | 0.416 | 0.3744 | 0.4576
488 | Bus488 | 1 | 0.416 | 0.3744 | 0.4576
489 | Bus489 | 1 | 0.416 | 0.3744 | 0.4576
490 | Bus490 | 1 | 0.416 | 0.3744 | 0.4576
491 | Bus491 | 1 | 0.416 | 0.3744 | 0.4576
492 | Bus492 | 1 | 0.416 | 0.3744 | 0.4576
493 | Bus493 | 1 | 0.416 | 0.3744 | 0.4576
494 | Bus494 | 1 | 0.416 | 0.3744 | 0.4576
495 | Bus495 | 1 | 0.416 | 0.3744 | 0.4576
496 | Bus496 | 1 | 0.416 | 0.3744 | 0.4576
497 | Bus497 | 1 | 0.416 | 0.3744 | 0.4576
498 | Bus498 | 1 | 0.416 | 0.3744 | 0.4576
499 | Bus499 | 1 | 0.416 | 0.3744 | 0.4576
500 | Bus500 | 1 | 0.416 | 0.3744 | 0.4576
501 | Bus501 | 1 | 0.416 | 0.3744 | 0.4576
502 | Bus502 | 1 | 0.416 | 0.3744 | 0.4576
503 | Bus503 | 1 | 0.416 | 0.3744 | 0.4576
504 | Bus504 | 1 | 0.416 | 0.3744 | 0.4576
505 | Bus505 | 1 | 0.416 | 0.3744 | 0.4576
506 | Bus506 | 1 | 0.416 | 0.3744 | 0.4576
507 | Bus507 | 1 | 0.416 | 0.3744 | 0.4576
508 | Bus508 | 1 | 0.416 | 0.3744 | 0.4576
509 | Bus509 | 1 | 0.416 | 0.3744 | 0.4576
510 | Bus510 | 1 | 0.416 | 0.3744 | 0.4576
511 | Bus511 | 1 | 0.416 | 0.3744 | 0.4576
512 | Bus512 | 1 | 0.416 | 0.3744 | 0.4576
513 | Bus513 | 1 | 0.416 | 0.3744 | 0.4576
514 | Bus514 | 1 | 0.416 | 0.3744 | 0.4576
515 | Bus515 | 1 | 0.416 | 0.3744 | 0.4576
516 | Bus516 | 1 | 0.416 | 0.3744 | 0.4576
517 | Bus517 | 1 | 0.416 | 0.3744 | 0.4576
518 | Bus518 | 1 | 0.416 | 0.3744 | 0.4576
519 | Bus519 | 1 | 0.416 | 0.3744 | 0.4576
520 | Bus520 | 1 | 0.416 | 0.3744 | 0.4576
521 | Bus521 | 1 | 0.416 | 0.3744 | 0.4576
522 | Bus522 | 1 | 0.416 | 0.3744 | 0.4576
523 | Bus523 | 1 | 0.416 | 0.3744 | 0.4576
524 | Bus524 | 1 | 0.416 | 0.3744 | 0.4576
525 | Bus525 | 1 | 0.416 | 0.3744 | 0.4576
526 | Bus526 | 1 | 0.416 | 0.3744 | 0.4576
527 | Bus527 | 1 | 0.416 | 0.3744 | 0.4576
528 | Bus528 | 1 | 0.416 | 0.3744 | 0.4576
529 | Bus529 | 1 | 0.416 | 0.3744 | 0.4576
530 | Bus530 | 1 | 0.416 | 0.3744 | 0.4576
531 | Bus531 | 1 | 0.416 | 0.3744 | 0.4576
532 | Bus532 | 1 | 0.416 | 0.3744 | 0.4576
533 | Bus533 | 1 | 0.416 | 0.3744 | 0.4576
534 | Bus534 | 1 | 0.416 | 0.3744 | 0.4576
535 | Bus535 | 1 | 0.416 | 0.3744 | 0.4576
536 | Bus536 | 1 | 0.416 | 0.3744 | 0.4576
537 | Bus537 | 1 | 0.416 | 0.3744 | 0.4576
538 | Bus538 | 1 | 0.416 | 0.3744 | 0.4576
539 | Bus539 | 1 | 0.416 | 0.3744 | 0.4576
540 | Bus540 | 1 | 0.416 | 0.3744 | 0.4576
541 | Bus541 | 1 | 0.416 | 0.3744 | 0.4576
542 | Bus542 | 1 | 0.416 | 0.3744 | 0.4576
543 | Bus543 | 1 | 0.416 | 0.3744 | 0.4576
544 | Bus544 | 1 | 0.416 | 0.3744 | 0.4576
545 | Bus545 | 1 | 0.416 | 0.3744 | 0.4576
546 | Bus546 | 1 | 0.416 | 0.3744 | 0.4576
547 | Bus547 | 1 | 0.416 | 0.3744 | 0.4576
548 | Bus548 | 1 | 0.416 | 0.3744 | 0.4576
549 | Bus549 | 1 | 0.416 | 0.3744 | 0.4576
550 | Bus550 | 1 | 0.416 | 0.3744 | 0.4576
551 | Bus551 | 1 | 0.416 | 0.3744 | 0.4576
552 | Bus552 | 1 | 0.416 | 0.3744 | 0.4576
553 | Bus553 | 1 | 0.416 | 0.3744 | 0.4576
554 | Bus554 | 1 | 0.416 | 0.3744 | 0.4576
555 | Bus555 | 1 | 0.416 | 0.3744 | 0.4576
556 | Bus556 | 1 | 0.416 | 0.3744 | 0.4576
557 | Bus557 | 1 | 0.416 | 0.3744 | 0.4576
558 | Bus558 | 1 | 0.416 | 0.3744 | 0.4576
559 | Bus559 | 1 | 0.416 | 0.3744 | 0.4576
560 | Bus560 | 1 | 0.416 | 0.3744 | 0.4576
561 | Bus561 | 1 | 0.416 | 0.3744 | 0.4576
562 | Bus562 | 1 | 0.416 | 0.3744 | 0.4576
563 | Bus563 | 1 | 0.416 | 0.3744 | 0.4576
564 | Bus564 | 1 | 0.416 | 0.3744 | 0.4576
565 | Bus565 | 1 | 0.416 | 0.3744 | 0.4576
566 | Bus566 | 1 | 0.416 | 0.3744 | 0.4576
567 | Bus567 | 1 | 0.416 | 0.3744 | 0.4576
568 | Bus568 | 1 | 0.416 | 0.3744 | 0.4576
569 | Bus569 | 1 | 0.416 | 0.3744 | 0.4576
570 | Bus570 | 1 | 0.416 | 0.3744 | 0.4576
571 | Bus571 | 1 | 0.416 | 0.3744 | 0.4576
572 | Bus572 | 1 | 0.416 | 0.3744 | 0.4576
573 | Bus573 | 1 | 0.416 | 0.3744 | 0.4576
574 | Bus574 | 1 | 0.416 | 0.3744 | 0.4576
575 | Bus575 | 1 | 0.416 | 0.3744 | 0.4576
576 | Bus576 | 1 | 0.416 | 0.3744 | 0.4576
577 | Bus577 | 1 | 0.416 | 0.3744 | 0.4576
578 | Bus578 | 1 | 0.416 | 0.3744 | 0.4576
579 | Bus579 | 1 | 0.416 | 0.3744 | 0.4576
580 | Bus580 | 1 | 0.416 | 0.3744 | 0.4576
581 | Bus581 | 1 | 0.416 | 0.3744 | 0.4576
582 | Bus582 | 1 | 0.416 | 0.3744 | 0.4576
583 | Bus583 | 1 | 0.416 | 0.3744 | 0.4576
584 | Bus584 | 1 | 0.416 | 0.3744 | 0.4576
585 | Bus585 | 1 | 0.416 | 0.3744 | 0.4576
586 | Bus586 | 1 | 0.416 | 0.3744 | 0.4576
587 | Bus587 | 1 | 0.416 | 0.3744 | 0.4576
588 | Bus588 | 1 | 0.416 | 0.3744 | 0.4576
589 | Bus589 | 1 | 0.416 | 0.3744 | 0.4576
590 | Bus590 | 1 | 0.416 | 0.3744 | 0.4576
591 | Bus591 | 1 | 0.416 | 0.3744 | 0.4576
592 | Bus592 | 1 | 0.416 | 0.3744 | 0.4576
593 | Bus593 | 1 | 0.416 | 0.3744 | 0.4576
594 | Bus594 | 1 | 0.416 | 0.3744 | 0.4576
595 | Bus595 | 1 | 0.416 | 0.3744 | 0.4576
596 | Bus596 | 1 | 0.416 | 0.3744 | 0.4576
597 | Bus597 | 1 | 0.416 | 0.3744 | 0.4576
598 | Bus598 | 1 | 0.416 | 0.3744 | 0.4576
599 | Bus599 | 1 | 0.416 | 0.3744 | 0.4576
600 | Bus600 | 1 | 0.416 | 0.3744 | 0.4576
601 | Bus601 | 1 | 0.416 | 0.3744 | 0.4576
602 | Bus602 | 1 | 0.416 | 0.3744 | 0.4576
603 | Bus603 | 1 | 0.416 | 0.3744 | 0.4576
604 | Bus604 | 1 | 0.416 | 0.3744 | 0.4576
605 | Bus605 | 1 | 0.416 | 0.3744 | 0.4576
606 | Bus606 | 1 | 0.416 | 0.3744 | 0.4576
607 | Bus607 | 1 | 0.416 | 0.3744 | 0.4576
608 | Bus608 | 1 | 0.416 | 0.3744 | 0.4576
609 | Bus609 | 1 | 0.416 | 0.3744 | 0.4576
610 | Bus610 | 1 | 0.416 | 0.3744 | 0.4576
611 | Bus611 | 1 | 0.416 | 0.3744 | 0.4576
612 | Bus612 | 1 | 0.416 | 0.3744 | 0.4576
613 | Bus613 | 1 | 0.416 | 0.3744 | 0.4576
614 | Bus614 | 1 | 0.416 | 0.3744 | 0.4576
615 | Bus615 | 1 | 0.416 | 0.3744 | 0.4576
616 | Bus616 | 1 | 0.416 | 0.3744 | 0.4576
617 | Bus617 | 1 | 0.416 | 0.3744 | 0.4576
618 | Bus618 | 1 | 0.416 | 0.3744 | 0.4576
619 | Bus619 | 1 | 0.416 | 0.3744 | 0.4576
620 | Bus620 | 1 | 0.416 | 0.3744 | 0.4576
621 | Bus621 | 1 | 0.416 | 0.3744 | 0.4576
622 | Bus622 | 1 | 0.416 | 0.3744 | 0.4576
623 | Bus623 | 1 | 0.416 | 0.3744 | 0.4576
624 | Bus624 | 1 | 0.416 | 0.3744 | 0.4576
625 | Bus625 | 1 | 0.416 | 0.3744 | 0.4576
626 | Bus626 | 1 | 0.416 | 0.3744 | 0.4576
627 | Bus627 | 1 | 0.416 | 0.3744 | 0.4576
628 | Bus628 | 1 | 0.416 | 0.3744 | 0.4576
629 | Bus629 | 1 | 0.416 | 0.3744 | 0.4576
630 | Bus630 | 1 | 0.416 | 0.3744 | 0.4576
631 | Bus631 | 1 | 0.416 | 0.3744 | 0.4576
632 | Bus632 | 1 | 0.416 | 0.3744 | 0.4576
633 | Bus633 | 1 | 0.416 | 0.3744 | 0.4576
634 | Bus634 | 1 | 0.416 | 0.3744 | 0.4576
635 | Bus635 | 1 | 0.416 | 0.3744 | 0.4576
636 | Bus636 | 1 | 0.416 | 0.3744 | 0.4576
637 | Bus637 | 1 | 0.416 | 0.3744 | 0.4576
638 | Bus638 | 1 | 0.416 | 0.3744 | 0.4576
639 | Bus639 | 1 | 0.416 | 0.3744 | 0.4576
640 | Bus640 | 1 | 0.416 | 0.3744 | 0.4576
641 | Bus641 | 1 | 0.416 | 0.3744 | 0.4576
642 | Bus642 | 1 | 0.416 | 0.3744 | 0.4576
643 | Bus643 | 1 | 0.416 | 0.3744 | 0.4576
644 | Bus644 | 1 | 0.416 | 0.3744 | 0.4576
645 | Bus645 | 1 | 0.416 | 0.3744 | 0.4576
646 | Bus646 | 1 | 0.416 | 0.3744 | 0.4576
647 | Bus647 | 1 | 0.416 | 0.3744 | 0.4576
648 | Bus648 | 1 | 0.416 | 0.3744 | 0.4576
649 | Bus649 | 1 | 0.416 | 0.3744 | 0.4576
650 | Bus650 | 1 | 0.416 | 0.3744 | 0.4576
651 | Bus651 | 1 | 0.416 | 0.3744 | 0.4576
652 | Bus652 | 1 | 0.416 | 0.3744 | 0.4576
653 | Bus653 | 1 | 0.416 | 0.3744 | 0.4576
654 | Bus654 | 1 | 0.416 | 0.3744 | 0.4576
655 | Bus655 | 1 | 0.416 | 0.3744 | 0.4576
656 | Bus656 | 1 | 0.416 | 0.3744 | 0.4576
657 | Bus657 | 1 | 0.416 | 0.3744 | 0.4576
658 | Bus658 | 1 | 0.416 | 0.3744 | 0.4576
659 | Bus659 | 1 | 0.416 | 0.3744 | 0.4576
660 | Bus660 | 1 | 0.416 | 0.3744 | 0.4576
661 | Bus661 | 1 | 0.416 | 0.3744 | 0.4576
662 | Bus662 | 1 | 0.416 | 0.3744 | 0.4576
663 | Bus663 | 1 | 0.416 | 0.3744 | 0.4576
664 | Bus664 | 1 | 0.416 | 0.3744 | 0.4576
665 | Bus665 | 1 | 0.416 | 0.3744 | 0.4576
666 | Bus666 | 1 | 0.416 | 0.3744 | 0.4576
667 | Bus667 | 1 | 0.416 | 0.3744 | 0.4576
668 | Bus668 | 1 | 0.416 | 0.3744 | 0.4576
669 | Bus669 | 1 | 0.416 | 0.3744 | 0.4576
670 | Bus670 | 1 | 0.416 | 0.3744 | 0.4576
671 | Bus671 | 1 | 0.416 | 0.3744 | 0.4576
672 | Bus672 | 1 | 0.416 | 0.3744 | 0.4576
673 | Bus673 | 1 | 0.416 | 0.3744 | 0.4576
674 | Bus674 | 1 | 0.416 | 0.3744 | 0.4576
675 | Bus675 | 1 | 0.416 | 0.3744 | 0.4576
676 | Bus676 | 1 | 0.416 | 0.3744 | 0.4576
677 | Bus677 | 1 | 0.416 | 0.3744 | 0.4576
678 | Bus678 | 1 | 0.416 | 0.3744 | 0.4576
679 | Bus679 | 1 | 0.416 | 0.3744 | 0.4576
680 | Bus680 | 1 | 0.416 | 0.3744 | 0.4576
681 | Bus681 | 1 | 0.416 | 0.3744 | 0.4576
682 | Bus682 | 1 | 0.416 | 0.3744 | 0.4576
683 | Bus683 | 1 | 0.416 | 0.3744 | 0.4576
684 | Bus684 | 1 | 0.416 | 0.3744 | 0.4576
685 | Bus685 | 1 | 0.416 | 0.3744 | 0.4576
686 | Bus686 | 1 | 0.416 | 0.3744 | 0.4576
687 | Bus687 | 1 | 0.416 | 0.3744 | 0.4576
688 | Bus688 | 1 | 0.416 | 0.3744 | 0.4576
689 | Bus689 | 1 | 0.416 | 0.3744 | 0.4576
690 | Bus690 | 1 | 0.416 | 0.3744 | 0.4576
691 | Bus691 | 1 | 0.416 | 0.3744 | 0.4576
692 | Bus692 | 1 | 0.416 | 0.3744 | 0.4576
693 | Bus693 | 1 | 0.416 | 0.3744 | 0.4576
694 | Bus694 | 1 | 0.416 | 0.3744 | 0.4576
695 | Bus695 | 1 | 0.416 | 0.3744 | 0.4576
696 | Bus696 | 1 | 0.416 | 0.3744 | 0.4576
697 | Bus697 | 1 | 0.416 | 0.3744 | 0.4576
698 | Bus698 | 1 | 0.416 | 0.3744 | 0.4576
699 | Bus699 | 1 | 0.416 | 0.3744 | 0.4576
700 | Bus700 | 1 | 0.416 | 0.3744 | 0.4576
701 | Bus701 | 1 | 0.416 | 0.3744 | 0.4576
702 | Bus702 | 1 | 0.416 | 0.3744 | 0.4576
703 | Bus703 | 1 | 0.416 | 0.3744 | 0.4576
704 | Bus704 | 1 | 0.416 | 0.3744 | 0.4576
705 | Bus705 | 1 | 0.416 | 0.3744 | 0.4576
706 | Bus706 | 1 | 0.416 | 0.3744 | 0.4576
707 | Bus707 | 1 | 0.416 | 0.3744 | 0.4576
708 | Bus708 | 1 | 0.416 | 0.3744 | 0.4576
709 | Bus709 | 1 | 0.416 | 0.3744 | 0.4576
710 | Bus710 | 1 | 0.416 | 0.3744 | 0.4576
711 | Bus711 | 1 | 0.416 | 0.3744 | 0.4576
712 | Bus712 | 1 | 0.416 | 0.3744 | 0.4576
713 | Bus713 | 1 | 0.416 | 0.3744 | 0.4576
714 | Bus714 | 1 | 0.416 | 0.3744 | 0.4576
715 | Bus715 | 1 | 0.416 | 0.3744 | 0.4576
716 | Bus716 | 1 | 0.416 | 0.3744 | 0.4576
717 | Bus717 | 1 | 0.416 | 0.3744 | 0.4576
718 | Bus718 | 1 | 0.416 | 0.3744 | 0.4576
719 | Bus719 | 1 | 0.416 | 0.3744 | 0.4576
720 | Bus720 | 1 | 0.416 | 0.3744 | 0.4576
721 | Bus721 | 1 | 0.416 | 0.3744 | 0.4576
722 | Bus722 | 1 | 0.416 | 0.3744 | 0.4576
723 | Bus723 | 1 | 0.416 | 0.3744 | 0.4576
724 | Bus724 | 1 | 0.416 | 0.3744 | 0.4576
725 | Bus725 | 1 | 0.416 | 0.3744 | 0.4576
726 | Bus726 | 1 | 0.416 | 0.3744 | 0.4576
727 | Bus727 | 1 | 0.416 | 0.3744 | 0.4576
728 | Bus728 | 1 | 0.416 | 0.3744 | 0.4576
729 | Bus729 | 1 | 0.416 | 0.3744 | 0.4576
730 | Bus730 | 1 | 0.416 | 0.3744 | 0.4576
731 | Bus731 | 1 | 0.416 | 0.3744 | 0.4576
732 | Bus732 | 1 | 0.416 | 0.3744 | 0.4576
733 | Bus733 | 1 | 0.416 | 0.3744 | 0.4576
734 | Bus734 | 1 | 0.416 | 0.3744 | 0.4576
735 | Bus735 | 1 | 0.416 | 0.3744 | 0.4576
736 | Bus736 | 1 | 0.416 | 0.3744 | 0.4576
737 | Bus737 | 1 | 0.416 | 0.3744 | 0.4576
738 | Bus738 | 1 | 0.416 | 0.3744 | 0.4576
739 | Bus739 | 1 | 0.416 | 0.3744 | 0.4576
740 | Bus740 | 1 | 0.416 | 0.3744 | 0.4576
741 | Bus741 | 1 | 0.416 | 0.3744 | 0.4576
742 | Bus742 | 1 | 0.416 | 0.3744 | 0.4576
743 | Bus743 | 1 | 0.416 | 0.3744 | 0.4576
744 | Bus744 | 1 | 0.416 | 0.3744 | 0.4576
745 | Bus745 | 1 | 0.416 | 0.3744 | 0.4576
746 | Bus746 | 1 | 0.416 | 0.3744 | 0.4576
747 | Bus747 | 1 | 0.416 | 0.3744 | 0.4576
748 | Bus748 | 1 | 0.416 | 0.3744 | 0.4576
749 | Bus749 | 1 | 0.416 | 0.3744 | 0.4576
750 | Bus750 | 1 | 0.416 | 0.3744 | 0.4576
751 | Bus751 | 1 | 0.416 | 0.3744 | 0.4576
752 | Bus752 | 1 | 0.416 | 0.3744 | 0.4576
753 | Bus753 | 1 | 0.416 | 0.3744 | 0.4576
754 | Bus754 | 1 | 0.416 | 0.3744 | 0.4576
755 | Bus755 | 1 | 0.416 | 0.3744 | 0.4576
756 | Bus756 | 1 | 0.416 | 0.3744 | 0.4576
757 | Bus757 | 1 | 0.416 | 0.3744 | 0.4576
758 | Bus758 | 1 | 0.416 | 0.3744 | 0.4576
759 | Bus759 | 1 | 0.416 | 0.3744 | 0.4576
760 | Bus760 | 1 | 0.416 | 0.3744 | 0.4576
761 | Bus761 | 1 | 0.416 | 0.3744 | 0.4576
762 | Bus762 | 1 | 0.416 | 0.3744 | 0.4576
763 | Bus763 | 1 | 0.416 | 0.3744 | 0.4576
764 | Bus764 | 1 | 0.416 | 0.3744 | 0.4576
765 | Bus765 | 1 | 0.416 | 0.3744 | 0.4576
766 | Bus766 | 1 | 0.416 | 0.3744 | 0.4576
767 | Bus767 | 1 | 0.416 | 0.3744 | 0.4576
768 | Bus768 | 1 | 0.416 | 0.3744 | 0.4576
769 | Bus769 | 1 | 0.416 | 0.3744 | 0.4576
770 | Bus770 | 1 | 0.416 | 0.3744 | 0.4576
771 | Bus771 | 1 | 0.416 | 0.3744 | 0.4576
772 | Bus772 | 1 | 0.416 | 0.3744 | 0.4576
773 | Bus773 | 1 | 0.416 | 0.3744 | 0.4576
774 | Bus774 | 1 | 0.416 | 0.3744 | 0.4576
775 | Bus775 | 1 | 0.416 | 0.3744 | 0.4576
776 | Bus776 | 1 | 0.416 | 0.3744 | 0.4576
777 | Bus777 | 1 | 0.416 | 0.3744 | 0.4576
778 | Bus778 | 1 | 0.416 | 0.3744 | 0.4576
779 | Bus779 | 1 | 0.416 | 0.3744 | 0.4576
780 | Bus780 | 1 | 0.416 | 0.3744 | 0.4576
781 | Bus781 | 1 | 0.416 | 0.3744 | 0.4576
782 | Bus782 | 1 | 0.416 | 0.3744 | 0.4576
783 | Bus783 | 1 | 0.416 | 0.3744 | 0.4576
784 | Bus784 | 1 | 0.416 | 0.3744 | 0.4576
785 | Bus785 | 1 | 0.416 | 0.3744 | 0.4576
786 | Bus786 | 1 | 0.416 | 0.3744 | 0.4576
787 | Bus787 | 1 | 0.416 | 0.3744 | 0.4576
788 | Bus788 | 1 | 0.416 | 0.3744 | 0.4576
789 | Bus789 | 1 | 0.416 | 0.3744 | 0.4576
790 | Bus790 | 1 | 0.416 | 0.3744 | 0.4576
791 | Bus791 | 1 | 0.416 | 0.3744 | 0.4576
792 | Bus792 | 1 | 0.416 | 0.3744 | 0.4576
793 | Bus793 | 1 | 0.416 | 0.3744 | 0.4576
794 | Bus794 | 1 | 0.416 | 0.3744 | 0.4576
795 | Bus795 | 1 | 0.416 | 0.3744 | 0.4576
796 | Bus796 | 1 | 0.416 | 0.3744 | 0.4576
797 | Bus797 | 1 | 0.416 | 0.3744 | 0.4576
798 | Bus798 | 1 | 0.416 | 0.3744 | 0.4576
799 | Bus799 | 1 | 0.416 | 0.3744 | 0.4576
800 | Bus800 | 1 | 0.416 | 0.3744 | 0.4576
801 | Bus801 | 1 | 0.416 | 0.3744 | 0.4576
802 | Bus802 | 1 | 0.416 | 0.3744 | 0.4576
803 | Bus803 | 1 | 0.416 | 0.3744 | 0.4576
804 | Bus804 | 1 | 0.416 | 0.3744 | 0.4576
805 | Bus805 | 1 | 0.416 | 0.3744 | 0.4576
806 | Bus806 | 1 | 0.416 | 0.3744 | 0.4576
807 | Bus807 | 1 | 0.416 | 0.3744 | 0.4576
808 | Bus808 | 1 | 0.416 | 0.3744 | 0.4576
809 | Bus809 | 1 | 0.416 | 0.3744 | 0.4576
810 | Bus810 | 1 | 0.416 | 0.3744 | 0.4576
811 | Bus811 | 1 | 0.416 | 0.3744 | 0.4576
812 | Bus812 | 1 | 0.416 | 0.3744 | 0.4576
813 | Bus813 | 1 | 0.416 | 0.3744 | 0.4576
814 | Bus814 | 1 | 0.416 | 0.3744 | 0.4576
815 | Bus815 | 1 | 0.416 | 0.3744 | 0.4576
816 | Bus816 | 1 | 0.416 | 0.3744 | 0.4576
817 | Bus817 | 1 | 0.416 | 0.3744 | 0.4576
818 | Bus818 | 1 | 0.416 | 0.3744 | 0.4576
819 | Bus819 | 1 | 0.416 | 0.3744 | 0.4576
820 | Bus820 | 1 | 0.416 | 0.3744 | 0.4576
821 | Bus821 | 1 | 0.416 | 0.3744 | 0.4576
822 | Bus822 | 1 | 0.416 | 0.3744 | 0.4576
823 | Bus823 | 1 | 0.416 | 0.3744 | 0.4576
824 | Bus824 | 1 | 0.416 | 0.3744 | 0.4576
825 | Bus825 | 1 | 0.416 | 0.3744 | 0.4576
826 | Bus826 | 1 | 0.416 | 0.3744 | 0.4576
827 | Bus827 | 1 | 0.416 | 0.3744 | 0.4576
828 | Bus828 | 1 | 0.416 | 0.3744 | 0.4576
829 | Bus829 | 1 | 0.416 | 0.3744 | 0.4576
830 | Bus830 | 1 | 0.416 | 0.3744 | 0.4576
831 | Bus831 | 1 | 0.416 | 0.3744 | 0.4576
832 | Bus832 | 1 | 0.416 | 0.3744 | 0.4576
833 | Bus833 | 1 | 0.416 | 0.3744 | 0.4576
834 | Bus834 | 1 | 0.416 | 0.3744 | 0.4576
835 | Bus835 | 1 | 0.416 | 0.3744 | 0.4576
836 | Bus836 | 1 | 0.416 | 0.3744 | 0.4576
837 | Bus837 | 1 | 0.416 | 0.3744 | 0.4576
838 | Bus838 | 1 | 0.416 | 0.3744 | 0.4576
839 | Bus839 | 1 | 0.416 | 0.3744 | 0.4576
840 | Bus840 | 1 | 0.416 | 0.3744 | 0.4576
841 | Bus841 | 1 | 0.416 | 0.3744 | 0.4576
842 | Bus842 | 1 | 0.416 | 0.3744 | 0.4576
843 | Bus843 | 1 | 0.416 | 0.3744 | 0.4576
844 | Bus844 | 1 | 0.416 | 0.3744 | 0.4576
845 | Bus845 | 1 | 0.416 | 0.3744 | 0.4576
846 | Bus846 | 1 | 0.416 | 0.3744 | 0.4576
847 | Bus847 | 1 | 0.416 | 0.3744 | 0.4576
848 | Bus848 | 1 | 0.416 | 0.3744 | 0.4576
849 | Bus849 | 1 | 0.416 | 0.3744 | 0.4576
850 | Bus850 | 1 | 0.416 | 0.3744 | 0.4576
851 | Bus851 | 1 | 0.416 | 0.3744 | 0.4576
852 | Bus852 | 1 | 0.416 | 0.3744 | 0.4576
853 | Bus853 | 1 | 0.416 | 0.3744 | 0.4576
854 | Bus854 | 1 | 0.416 | 0.3744 | 0.4576
855 | Bus855 | 1 | 0.416 | 0.3744 | 0.4576
856 | Bus856 | 1 | 0.416 | 0.3744 | 0.4576
857 | Bus857 | 1 | 0.416 | 0.3744 | 0.4576
858 | Bus858 | 1 | 0.416 | 0.3744 | 0.4576
859 | Bus859 | 1 | 0.416 | 0.3744 | 0.4576
860 | Bus860 | 1 | 0.416 | 0.3744 | 0.4576
861 | Bus861 | 1 | 0.416 | 0.3744 | 0.4576
862 | Bus862 | 1 | 0.416 | 0.3744 | 0.4576
863 | Bus863 | 1 | 0.416 | 0.3744 | 0.4576
864 | Bus864 | 1 | 0.416 | 0.3744 | 0.4576
865 | Bus865 | 1 | 0.416 | 0.3744 | 0.4576
866 | Bus866 | 1 | 0.416 | 0.3744 | 0.4576
867 | Bus867 | 1 | 0.416 | 0.3744 | 0.4576
868 | Bus868 | 1 | 0.416 | 0.3744 | 0.4576
869 | Bus869 | 1 | 0.416 | 0.3744 | 0.4576
870 | Bus870 | 1 | 0.416 | 0.3744 | 0.4576
871 | Bus871 | 1 | 0.416 | 0.3744 | 0.4576
872 | Bus872 | 1 | 0.416 | 0.3744 | 0.4576
873 | Bus873 | 1 | 0.416 | 0.3744 | 0.4576
874 | Bus874 | 1 | 0.416 | 0.3744 | 0.4576
875 | Bus875 | 1 | 0.416 | 0.3744 | 0.4576
876 | Bus876 | 1 | 0.416 | 0.3744 | 0.4576
877 | Bus877 | 1 | 0.416 | 0.3744 | 0.4576
878 | Bus878 | 1 | 0.416 | 0.3744 | 0.4576
879 | Bus879 | 1 | 0.416 | 0.3744 | 0.4576
880 | Bus880 | 1 | 0.416 | 0.3744 | 0.4576
881 | Bus881 | 1 | 0.416 | 0.3744 | 0.4576
882 | Bus882 | 1 | 0.416 | 0.3744 | 0.4576
883 | Bus883 | 1 | 0.416 | 0.3744 | 0.4576
884 | Bus884 | 1 | 0.416 | 0.3744 | 0.4576
885 | Bus885 | 1 | 0.416 | 0.3744 | 0.4576
886 | Bus886 | 1 | 0.416 | 0.3744 | 0.4576
887 | Bus887 | 1 | 0.416 | 0.3744 | 0.4576
888 | Bus888 | 1 | 0.416 | 0.3744 | 0.4576
889 | Bus889 | 1 | 0.416 | 0.3744 | 0.4576
890 | Bus890 | 1 | 0.416 | 0.3744 | 0.4576
891 | Bus891 | 1 | 0.416 | 0.3744 | 0.4576
892 | Bus892 | 1 | 0.416 | 0.3744 | 0.4576
893 | Bus893 | 1 | 0.416 | 0.3744 | 0.4576
894 | Bus894 | 1 | 0.416 | 0.3744 | 0.4576
895 | Bus895 | 1 | 0.416 | 0.3744 | 0.4576
896 | Bus896 | 1 | 0.416 | 0.3744 | 0.4576
897 | Bus897 | 1 | 0.416 | 0.3744 | 0.4576
898 | Bus898 | 1 | 0.416 | 0.3744 | 0.4576
899 | Bus899 | 1 | 0.416 | 0.3744 | 0.4576
900 | Bus900 | 1 | 0.416 | 0.3744 | 0.4576
901 | Bus901 | 1 | 0.416 | 0.3744 | 0.4576
902 | Bus902 | 1 | 0.416 | 0.3744 | 0.4576
903 | Bus903 | 1 | 0.416 | 0.3744 | 0.4576
904 | Bus904 | 1 | 0.416 | 0.3744 | 0.4576
905 | Bus905 | 1 | 0.416 | 0.3744 | 0.4576
906 | Bus906 | 1 | 0.416 | 0.3744 | 0.4576
1000 | Bus1000 | 1 | 11 | 9.9 | 12.1
1001 | Bus1001 | 1 | 11 | 9.9 | 12.1

## Branch
BranchNo | FromNode | ToNodeB | Length (ft) | Config | Status
1 | 1 | 2 | 5.7974 | 78 | 1
2 | 2 | 3 | 0.60778 | 78 | 1
3 | 3 | 4 | 0.56939 | 78 | 1
4 | 4 | 5 | 0.49643 | 78 | 1
5 | 5 | 6 | 0.78207 | 78 | 1
6 | 6 | 7 | 53.2555 | 78 | 1
7 | 7 | 8 | 2.3852 | 78 | 1
8 | 8 | 9 | 1.9853 | 78 | 1
9 | 9 | 10 | 1.7422 | 78 | 1
10 | 10 | 11 | 1.3 | 78 | 1
11 | 11 | 12 | 1.2204 | 78 | 1
12 | 12 | 13 | 0.75044 | 78 | 1
13 | 13 | 14 | 1.8683 | 78 | 1
14 | 14 | 15 | 15.1346 | 78 | 1
15 | 15 | 16 | 0.50973 | 70 | 1
16 | 15 | 17 | 18.3532 | 78 | 1
17 | 16 | 18 | 0.23256 | 70 | 1
18 | 17 | 19 | 1.2628 | 78 | 1
19 | 18 | 20 | 0.2438 | 70 | 1
20 | 19 | 21 | 1.418 | 78 | 1
21 | 20 | 22 | 0.22163 | 70 | 1
22 | 21 | 23 | 2.3088 | 78 | 1
23 | 22 | 24 | 0.27057 | 70 | 1
24 | 23 | 25 | 4.2002 | 78 | 1
25 | 24 | 26 | 0.29516 | 70 | 1
26 | 25 | 27 | 31.1778 | 72 | 1
27 | 25 | 28 | 52.6341 | 78 | 1
28 | 26 | 29 | 0.28809 | 70 | 1
29 | 27 | 30 | 8.5879 | 72 | 1
30 | 27 | 31 | 8.3672 | 72 | 1
31 | 28 | 32 | 14.012 | 78 | 1
32 | 29 | 33 | 0.77241 | 70 | 1
33 | 30 | 34 | 19.6669 | 72 | 1
34 | 31 | 35 | 0.28336 | 72 | 1
35 | 32 | 36 | 30.2358 | 72 | 1
36 | 32 | 37 | 42.3687 | 78 | 1
37 | 33 | 38 | 0.72061 | 70 | 1
38 | 35 | 39 | 0.40741 | 72 | 1
39 | 36 | 40 | 2.1122 | 72 | 1
40 | 36 | 41 | 9.5372 | 72 | 1
41 | 37 | 42 | 29.4011 | 78 | 1
42 | 37 | 43 | 1.1444 | 77 | 1
43 | 38 | 44 | 0.17866 | 70 | 1
44 | 39 | 45 | 0.52248 | 72 | 1
45 | 40 | 46 | 0.95203 | 72 | 1
46 | 41 | 47 | 22.9484 | 72 | 1
47 | 42 | 48 | 22.2171 | 78 | 1
48 | 43 | 49 | 0.55102 | 77 | 1
49 | 44 | 50 | 0.25399 | 70 | 1
50 | 45 | 51 | 1.2725 | 72 | 1
51 | 46 | 52 | 1.009 | 72 | 1
52 | 48 | 53 | 3.2033 | 78 | 1
53 | 48 | 54 | 3.3765 | 78 | 1
54 | 49 | 55 | 0.6138 | 77 | 1
55 | 50 | 56 | 0.46286 | 70 | 1
56 | 51 | 57 | 1.0895 | 72 | 1
57 | 52 | 58 | 0.96096 | 72 | 1
58 | 53 | 59 | 14.5099 | 78 | 1
59 | 54 | 60 | 0.34514 | 78 | 1
60 | 55 | 61 | 0.52948 | 77 | 1
61 | 56 | 62 | 0.41184 | 70 | 1
62 | 57 | 63 | 5.2225 | 72 | 1
63 | 58 | 64 | 0.57552 | 72 | 1
64 | 59 | 65 | 2.9498 | 78 | 1
65 | 59 | 66 | 43.6037 | 72 | 1
66 | 60 | 67 | 0.39072 | 78 | 1
67 | 61 | 68 | 0.5071 | 77 | 1
68 | 62 | 69 | 0.43951 | 70 | 1
69 | 63 | 70 | 18.4599 | 72 | 1
70 | 64 | 71 | 1.1291 | 72 | 1
71 | 65 | 72 | 34.8511 | 78 | 1
72 | 66 | 73 | 21.3132 | 72 | 1
73 | 66 | 74 | 21.3132 | 72 | 1
74 | 67 | 75 | 0.94781 | 78 | 1
75 | 68 | 76 | 1.2435 | 77 | 1
76 | 69 | 77 | 2.0543 | 70 | 1
77 | 71 | 78 | 5.7224 | 72 | 1
78 | 72 | 79 | 12.1482 | 78 | 1
79 | 75 | 80 | 0.54711 | 78 | 1
80 | 76 | 81 | 3.9436 | 77 | 1
81 | 77 | 82 | 2.6974 | 70 | 1
82 | 78 | 83 | 21.5635 | 72 | 1
83 | 79 | 84 | 2.6511 | 78 | 1
84 | 80 | 85 | 0.58724 | 78 | 1
85 | 81 | 86 | 7.5968 | 77 | 1
86 | 82 | 87 | 1.6392 | 70 | 1
87 | 84 | 88 | 5.3761 | 78 | 1
88 | 85 | 89 | 0.55334 | 78 | 1
89 | 86 | 90 | 1.8084 | 77 | 1
90 | 87 | 91 | 0.59168 | 70 | 1
91 | 88 | 92 | 5.0699 | 78 | 1
92 | 90 | 93 | 0.34482 | 77 | 1
93 | 91 | 94 | 0.18366 | 70 | 1
94 | 92 | 95 | 2.9468 | 78 | 1
95 | 93 | 96 | 0.45435 | 77 | 1
96 | 94 | 97 | 0.19415 | 70 | 1
97 | 95 | 98 | 1.9462 | 78 | 1
98 | 96 | 99 | 0.1965 | 77 | 1
99 | 97 | 100 | 0.47302 | 70 | 1
100 | 98 | 101 | 2.6871 | 78 | 1
101 | 99 | 102 | 26.8324 | 77 | 1
102 | 100 | 103 | 1.5092 | 70 | 1
103 | 101 | 104 | 1.5226 | 76 | 1
104 | 101 | 105 | 1.7742 | 78 | 1
105 | 102 | 106 | 1.1673 | 77 | 1
106 | 104 | 107 | 1.8422 | 76 | 1
107 | 105 | 108 | 1.006 | 78 | 1
108 | 106 | 109 | 2.3805 | 77 | 1
109 | 107 | 110 | 2.1352 | 76 | 1
110 | 108 | 111 | 39.696 | 78 | 1
111 | 109 | 112 | 63.2363 | 77 | 1
112 | 110 | 113 | 3.2556 | 76 | 1
113 | 111 | 114 | 3.9767 | 78 | 1
114 | 112 | 115 | 56.2915 | 77 | 1
115 | 113 | 116 | 4.1855 | 76 | 1
116 | 114 | 117 | 5.8376 | 76 | 1
117 | 114 | 118 | 19.3015 | 75 | 1
118 | 115 | 119 | 5.2517 | 77 | 1
119 | 116 | 120 | 3.0048 | 76 | 1
120 | 117 | 121 | 1.0286 | 70 | 1
121 | 117 | 122 | 2.8423 | 76 | 1
122 | 118 | 123 | 34.8078 | 75 | 1
123 | 119 | 124 | 3.8269 | 77 | 1
124 | 120 | 125 | 4.2457 | 76 | 1
125 | 121 | 126 | 0.89068 | 70 | 1
126 | 122 | 127 | 13.352 | 76 | 1
127 | 123 | 128 | 15.653 | 75 | 1
128 | 124 | 129 | 3.3006 | 77 | 1
129 | 125 | 130 | 4.5936 | 76 | 1
130 | 126 | 131 | 0.62911 | 70 | 1
131 | 127 | 132 | 20.1759 | 72 | 1
132 | 127 | 133 | 37.9008 | 76 | 1
133 | 128 | 134 | 4.6572 | 75 | 1
134 | 129 | 135 | 10.1392 | 77 | 1
135 | 130 | 136 | 4.3321 | 76 | 1
136 | 131 | 137 | 0.97342 | 70 | 1
137 | 132 | 138 | 1.7375 | 72 | 1
138 | 133 | 139 | 28.1962 | 76 | 1
139 | 134 | 140 | 5.2571 | 75 | 1
140 | 135 | 141 | 7.459 | 77 | 1
141 | 136 | 142 | 7.1227 | 76 | 1
142 | 137 | 143 | 1.15 | 70 | 1
143 | 138 | 144 | 1.7049 | 72 | 1
144 | 139 | 145 | 18.8823 | 76 | 1
145 | 140 | 146 | 4.9442 | 75 | 1
146 | 141 | 147 | 1.27 | 77 | 1
147 | 142 | 148 | 33.8669 | 76 | 1
148 | 143 | 149 | 1.0244 | 70 | 1
149 | 144 | 150 | 1.3766 | 72 | 1
150 | 145 | 151 | 18.8564 | 76 | 1
151 | 145 | 152 | 27.0937 | 72 | 1
152 | 146 | 153 | 5.7689 | 75 | 1
153 | 147 | 154 | 0.43875 | 77 | 1
154 | 148 | 155 | 7.3777 | 76 | 1
155 | 149 | 156 | 1.1568 | 70 | 1
156 | 150 | 157 | 2.0662 | 72 | 1
157 | 151 | 158 | 50.0083 | 76 | 1
158 | 152 | 159 | 1.6491 | 72 | 1
159 | 153 | 160 | 1.66 | 75 | 1
160 | 154 | 161 | 0.64712 | 77 | 1
161 | 155 | 162 | 61.9987 | 72 | 1
162 | 155 | 163 | 27.9016 | 76 | 1
163 | 156 | 164 | 1.0741 | 70 | 1
164 | 157 | 165 | 2.491 | 72 | 1
165 | 158 | 166 | 17.3706 | 76 | 1
166 | 159 | 167 | 1.5065 | 72 | 1
167 | 160 | 168 | 9.4306 | 75 | 1
168 | 161 | 169 | 1.3178 | 77 | 1
169 | 162 | 170 | 11.7126 | 72 | 1
170 | 163 | 171 | 37.0423 | 76 | 1
171 | 164 | 172 | 0.91185 | 70 | 1
172 | 165 | 173 | 1.8819 | 72 | 1
173 | 166 | 174 | 20.6886 | 76 | 1
174 | 166 | 175 | 22.1997 | 72 | 1
175 | 167 | 176 | 0.62584 | 72 | 1
176 | 168 | 177 | 5.3265 | 75 | 1
177 | 170 | 178 | 24.1654 | 72 | 1
178 | 171 | 179 | 6.2399 | 76 | 1
179 | 171 | 180 | 12.7902 | 72 | 1
180 | 172 | 181 | 0.94834 | 70 | 1
181 | 173 | 182 | 2.1777 | 72 | 1
182 | 174 | 183 | 3.1027 | 76 | 1
183 | 175 | 184 | 2.3976 | 72 | 1
184 | 176 | 185 | 1.349 | 72 | 1
185 | 177 | 186 | 3.954 | 75 | 1
186 | 179 | 187 | 24.5556 | 76 | 1
187 | 180 | 188 | 52.9361 | 72 | 1
188 | 181 | 189 | 0.81375 | 70 | 1
189 | 182 | 190 | 2.0476 | 72 | 1
190 | 183 | 191 | 12.2237 | 76 | 1
191 | 183 | 192 | 1.4674 | 76 | 1
192 | 184 | 193 | 2.3191 | 72 | 1
193 | 185 | 194 | 3.4358 | 72 | 1
194 | 186 | 195 | 3.5548 | 75 | 1
195 | 187 | 196 | 43.8429 | 76 | 1
196 | 188 | 197 | 10.3461 | 72 | 1
197 | 188 | 198 | 5.9796 | 72 | 1
198 | 189 | 199 | 1.011 | 70 | 1
199 | 190 | 200 | 2.2031 | 72 | 1
200 | 191 | 201 | 4.9178 | 76 | 1
201 | 192 | 202 | 0.8684 | 76 | 1
202 | 193 | 203 | 1.8551 | 72 | 1
203 | 194 | 204 | 2.0158 | 72 | 1
204 | 195 | 205 | 4.4161 | 75 | 1
205 | 196 | 206 | 17.1468 | 72 | 1
206 | 196 | 207 | 11.2839 | 76 | 1
207 | 197 | 208 | 26.1576 | 72 | 1
208 | 198 | 209 | 0.84522 | 72 | 1
209 | 199 | 210 | 2.3674 | 70 | 1
210 | 200 | 211 | 3.3678 | 72 | 1
211 | 202 | 212 | 0.81977 | 76 | 1
212 | 203 | 213 | 1.4777 | 72 | 1
213 | 204 | 214 | 1.4119 | 72 | 1
214 | 205 | 215 | 8.1491 | 75 | 1
215 | 206 | 216 | 56.1236 | 72 | 1
216 | 207 | 217 | 20.3654 | 76 | 1
217 | 209 | 218 | 0.68165 | 72 | 1
218 | 210 | 219 | 3.5489 | 70 | 1
219 | 211 | 220 | 9.1972 | 72 | 1
220 | 212 | 221 | 0.89791 | 76 | 1
221 | 213 | 222 | 3.1241 | 72 | 1
222 | 214 | 223 | 2.7159 | 72 | 1
223 | 215 | 224 | 7.1048 | 75 | 1
224 | 216 | 225 | 24.194 | 72 | 1
225 | 217 | 226 | 7.2716 | 76 | 1
226 | 218 | 227 | 0.54474 | 72 | 1
227 | 220 | 228 | 0.78418 | 72 | 1
228 | 221 | 229 | 1.2288 | 76 | 1
229 | 222 | 230 | 2.4603 | 72 | 1
230 | 223 | 231 | 1.3518 | 72 | 1
231 | 224 | 232 | 4.833 | 75 | 1
232 | 226 | 233 | 62.8049 | 72 | 1
233 | 226 | 234 | 5.9521 | 76 | 1
234 | 227 | 235 | 0.83155 | 72 | 1
235 | 228 | 236 | 0.36221 | 72 | 1
236 | 229 | 237 | 1.0952 | 76 | 1
237 | 230 | 238 | 1.7066 | 72 | 1
238 | 231 | 239 | 0.95985 | 72 | 1
239 | 232 | 240 | 3.1749 | 75 | 1
240 | 233 | 241 | 9.1206 | 72 | 1
241 | 235 | 242 | 0.97474 | 72 | 1
242 | 236 | 243 | 0.38742 | 72 | 1
243 | 237 | 244 | 0.89131 | 76 | 1
244 | 238 | 245 | 1.7025 | 72 | 1
245 | 239 | 246 | 10.9803 | 72 | 1
246 | 240 | 247 | 6.8328 | 75 | 1
247 | 241 | 248 | 27.9955 | 72 | 1
248 | 241 | 249 | 27.9955 | 72 | 1
249 | 242 | 250 | 1.4971 | 72 | 1
250 | 243 | 251 | 0.3702 | 72 | 1
251 | 244 | 252 | 0.70208 | 76 | 1
252 | 245 | 253 | 2.4907 | 72 | 1
253 | 246 | 254 | 3.2379 | 72 | 1
254 | 247 | 255 | 24.0862 | 72 | 1
255 | 247 | 256 | 4.5238 | 75 | 1
256 | 250 | 257 | 5.4785 | 72 | 1
257 | 251 | 258 | 0.41242 | 72 | 1
258 | 252 | 259 | 0.91465 | 76 | 1
259 | 253 | 260 | 9.3678 | 72 | 1
260 | 254 | 261 | 0.72441 | 72 | 1
261 | 255 | 262 | 3.3296 | 72 | 1
262 | 256 | 263 | 16.9635 | 75 | 1
263 | 257 | 264 | 26.6639 | 72 | 1
264 | 258 | 265 | 0.85129 | 72 | 1
265 | 259 | 266 | 1.0262 | 76 | 1
266 | 260 | 267 | 2.1864 | 72 | 1
267 | 261 | 268 | 18.2571 | 72 | 1
268 | 261 | 269 | 0.62679 | 72 | 1
269 | 262 | 270 | 1.5307 | 72 | 1
270 | 263 | 271 | 22.4648 | 72 | 1
271 | 263 | 272 | 5.6982 | 75 | 1
272 | 265 | 273 | 0.88662 | 72 | 1
273 | 266 | 274 | 0.94448 | 76 | 1
274 | 267 | 275 | 1.0017 | 72 | 1
275 | 268 | 276 | 18.0935 | 72 | 1
276 | 269 | 277 | 0.73487 | 72 | 1
277 | 270 | 278 | 1.8181 | 72 | 1
278 | 271 | 279 | 1.6329 | 72 | 1
279 | 272 | 280 | 20.6558 | 75 | 1
280 | 273 | 281 | 3.3715 | 72 | 1
281 | 274 | 282 | 3.1966 | 76 | 1
282 | 275 | 283 | 0.65852 | 72 | 1
283 | 277 | 284 | 0.66412 | 72 | 1
284 | 278 | 285 | 2.805 | 72 | 1
285 | 279 | 286 | 1.3459 | 72 | 1
286 | 280 | 287 | 9.2622 | 74 | 1
287 | 280 | 288 | 4.8209 | 75 | 1
288 | 281 | 289 | 17.8997 | 72 | 1
289 | 282 | 290 | 4.2791 | 76 | 1
290 | 283 | 291 | 4.6262 | 72 | 1
291 | 283 | 292 | 0.57061 | 72 | 1
292 | 284 | 293 | 0.67262 | 72 | 1
293 | 285 | 294 | 2.4995 | 72 | 1
294 | 286 | 295 | 1.9118 | 72 | 1
295 | 287 | 296 | 4.2632 | 74 | 1
296 | 288 | 297 | 20.2044 | 75 | 1
297 | 291 | 298 | 2.1251 | 72 | 1
298 | 292 | 299 | 0.40384 | 72 | 1
299 | 293 | 300 | 0.7232 | 72 | 1
300 | 294 | 301 | 1.9433 | 72 | 1
301 | 295 | 302 | 8.5868 | 72 | 1
302 | 296 | 303 | 27.8498 | 74 | 1
303 | 297 | 304 | 4.4599 | 75 | 1
304 | 298 | 305 | 3.5967 | 72 | 1
305 | 299 | 306 | 0.46995 | 72 | 1
306 | 300 | 307 | 4.1942 | 72 | 1
307 | 301 | 308 | 2.4189 | 72 | 1
308 | 302 | 309 | 1.6531 | 72 | 1
309 | 303 | 310 | 2.0802 | 74 | 1
310 | 304 | 311 | 1.4819 | 75 | 1
311 | 305 | 312 | 6.9036 | 72 | 1
312 | 306 | 313 | 0.89886 | 72 | 1
313 | 307 | 314 | 17.7397 | 72 | 1
314 | 308 | 315 | 2.5019 | 72 | 1
315 | 309 | 316 | 1.224 | 72 | 1
316 | 310 | 317 | 3.4269 | 72 | 1
317 | 310 | 318 | 38.102 | 74 | 1
318 | 311 | 319 | 0.77347 | 75 | 1
319 | 312 | 320 | 20.3253 | 72 | 1
320 | 313 | 321 | 3.4473 | 72 | 1
321 | 315 | 322 | 2.9511 | 72 | 1
322 | 316 | 323 | 1.4099 | 72 | 1
323 | 317 | 324 | 17.6494 | 72 | 1
324 | 318 | 325 | 18.2851 | 74 | 1
325 | 319 | 326 | 0.66211 | 75 | 1
326 | 321 | 327 | 11.7643 | 72 | 1
327 | 322 | 328 | 1.6817 | 72 | 1
328 | 323 | 329 | 1.3986 | 72 | 1
329 | 324 | 330 | 6.1617 | 72 | 1
330 | 325 | 331 | 48.2232 | 72 | 1
331 | 325 | 332 | 35.2328 | 74 | 1
332 | 326 | 333 | 0.75303 | 75 | 1
333 | 328 | 334 | 7.5974 | 72 | 1
334 | 329 | 335 | 12.2865 | 72 | 1
335 | 330 | 336 | 13.4106 | 72 | 1
336 | 331 | 337 | 19.0988 | 72 | 1
337 | 332 | 338 | 35.9393 | 72 | 1
338 | 332 | 339 | 6.4041 | 74 | 1
339 | 333 | 340 | 0.59326 | 75 | 1
340 | 334 | 341 | 2.9567 | 72 | 1
341 | 335 | 342 | 25.1153 | 72 | 1
342 | 336 | 343 | 10.9929 | 72 | 1
343 | 336 | 344 | 5.1723 | 72 | 1
344 | 338 | 345 | 18.0686 | 72 | 1
345 | 339 | 346 | 5.4864 | 74 | 1
346 | 340 | 347 | 0.49739 | 75 | 1
347 | 341 | 348 | 1.0272 | 72 | 1
348 | 343 | 349 | 16.4487 | 72 | 1
349 | 344 | 350 | 0.72019 | 72 | 1
350 | 345 | 351 | 1.6815 | 72 | 1
351 | 346 | 352 | 3.8592 | 74 | 1
352 | 347 | 353 | 0.4488 | 75 | 1
353 | 348 | 354 | 0.77383 | 72 | 1
354 | 350 | 355 | 0.78218 | 72 | 1
355 | 351 | 356 | 0.69442 | 72 | 1
356 | 352 | 357 | 4.8762 | 74 | 1
357 | 353 | 358 | 0.37144 | 75 | 1
358 | 354 | 359 | 0.56617 | 72 | 1
359 | 355 | 360 | 0.68513 | 72 | 1
360 | 356 | 361 | 0.48999 | 72 | 1
361 | 357 | 362 | 3.0554 | 74 | 1
362 | 358 | 363 | 0.43089 | 75 | 1
363 | 359 | 364 | 0.28751 | 72 | 1
364 | 360 | 365 | 0.72795 | 72 | 1
365 | 361 | 366 | 0.50118 | 72 | 1
366 | 362 | 367 | 4.6918 | 74 | 1
367 | 363 | 368 | 0.47358 | 75 | 1
368 | 364 | 369 | 0.42269 | 72 | 1
369 | 365 | 370 | 1.0389 | 72 | 1
370 | 366 | 371 | 0.59136 | 72 | 1
371 | 367 | 372 | 4.6772 | 74 | 1
372 | 368 | 373 | 2.5818 | 75 | 1
373 | 369 | 374 | 0.70857 | 72 | 1
374 | 370 | 375 | 1.263 | 72 | 1
375 | 371 | 376 | 0.74596 | 72 | 1
376 | 372 | 377 | 5.248 | 74 | 1
377 | 373 | 378 | 19.4557 | 75 | 1
378 | 373 | 379 | 7.4527 | 72 | 1
379 | 374 | 380 | 3.1605 | 72 | 1
380 | 375 | 381 | 7.8286 | 72 | 1
381 | 376 | 382 | 0.66808 | 72 | 1
382 | 377 | 383 | 3.7976 | 74 | 1
383 | 378 | 384 | 18.6341 | 75 | 1
384 | 379 | 385 | 45.7606 | 72 | 1
385 | 379 | 386 | 7.6882 | 72 | 1
386 | 380 | 387 | 11.6181 | 72 | 1
387 | 381 | 388 | 26.7875 | 72 | 1
388 | 382 | 389 | 0.52863 | 72 | 1
389 | 383 | 390 | 4.5264 | 74 | 1
390 | 384 | 391 | 0.82954 | 75 | 1
391 | 385 | 392 | 16.7244 | 72 | 1
392 | 386 | 393 | 41.3608 | 72 | 1
393 | 389 | 394 | 0.90726 | 72 | 1
394 | 390 | 395 | 6.5678 | 74 | 1
395 | 391 | 396 | 21.4373 | 72 | 1
396 | 391 | 397 | 15.2027 | 75 | 1
397 | 392 | 398 | 1.7023 | 72 | 1
398 | 393 | 399 | 3.0033 | 72 | 1
399 | 394 | 400 | 3.1671 | 72 | 1
400 | 395 | 401 | 4.8692 | 74 | 1
401 | 396 | 402 | 1.9642 | 72 | 1
402 | 397 | 403 | 7.3344 | 75 | 1
403 | 398 | 404 | 1.188 | 72 | 1
404 | 399 | 405 | 1.3098 | 72 | 1
405 | 400 | 406 | 19.3628 | 72 | 1
406 | 401 | 407 | 4.6971 | 74 | 1
407 | 402 | 408 | 1.1166 | 72 | 1
408 | 403 | 409 | 22.1268 | 75 | 1
409 | 403 | 410 | 2.0016 | 75 | 1
410 | 404 | 411 | 1.2307 | 72 | 1
411 | 405 | 412 | 0.88207 | 72 | 1
412 | 407 | 413 | 4.5971 | 74 | 1
413 | 408 | 414 | 0.75821 | 72 | 1
414 | 409 | 415 | 31.5141 | 75 | 1
415 | 410 | 416 | 0.50118 | 75 | 1
416 | 411 | 417 | 5.1681 | 72 | 1
417 | 412 | 418 | 1.476 | 72 | 1
418 | 413 | 419 | 5.5287 | 74 | 1
419 | 414 | 420 | 1.2357 | 72 | 1
420 | 415 | 421 | 6.5947 | 75 | 1
421 | 416 | 422 | 0.3515 | 75 | 1
422 | 417 | 423 | 1.2619 | 72 | 1
423 | 418 | 424 | 16.8664 | 72 | 1
424 | 419 | 425 | 9.2595 | 74 | 1
425 | 419 | 426 | 9.2595 | 74 | 1
426 | 420 | 427 | 4.1075 | 72 | 1
427 | 421 | 428 | 1.6855 | 75 | 1
428 | 422 | 429 | 0.43757 | 75 | 1
429 | 423 | 430 | 1.2037 | 72 | 1
430 | 424 | 431 | 5.9828 | 72 | 1
431 | 425 | 432 | 31.2317 | 74 | 1
432 | 425 | 433 | 31.2317 | 74 | 1
433 | 427 | 434 | 4.5729 | 72 | 1
434 | 428 | 435 | 0.88303 | 75 | 1
435 | 429 | 436 | 0.3767 | 75 | 1
436 | 430 | 437 | 1.1972 | 72 | 1
437 | 431 | 438 | 2.0275 | 72 | 1
438 | 432 | 439 | 44.174 | 74 | 1
439 | 432 | 440 | 44.174 | 74 | 1
440 | 434 | 441 | 2.5718 | 72 | 1
441 | 435 | 442 | 0.73202 | 75 | 1
442 | 436 | 443 | 0.41184 | 75 | 1
443 | 437 | 444 | 1.3733 | 72 | 1
444 | 438 | 445 | 3.5829 | 72 | 1
445 | 439 | 446 | 31.6973 | 74 | 1
446 | 439 | 447 | 31.6973 | 74 | 1
447 | 441 | 448 | 2.4159 | 72 | 1
448 | 442 | 449 | 0.59326 | 75 | 1
449 | 443 | 450 | 0.41842 | 75 | 1
450 | 444 | 451 | 4.7427 | 72 | 1
451 | 445 | 452 | 3.1345 | 72 | 1
452 | 446 | 453 | 9.617 | 74 | 1
453 | 446 | 454 | 9.617 | 74 | 1
454 | 448 | 455 | 2.305 | 72 | 1
455 | 449 | 456 | 0.90684 | 75 | 1
456 | 450 | 457 | 0.28634 | 75 | 1
457 | 451 | 458 | 23.1121 | 72 | 1
458 | 452 | 459 | 3.541 | 72 | 1
459 | 453 | 460 | 28.4618 | 74 | 1
460 | 453 | 461 | 28.4618 | 74 | 1
461 | 453 | 462 | 19.4615 | 72 | 1
462 | 455 | 463 | 3.7844 | 72 | 1
463 | 456 | 464 | 0.8175 | 75 | 1
464 | 457 | 465 | 0.21284 | 75 | 1
465 | 459 | 466 | 3.3486 | 72 | 1
466 | 460 | 467 | 31.6224 | 74 | 1
467 | 460 | 468 | 31.6224 | 74 | 1
468 | 460 | 469 | 4.6618 | 74 | 1
469 | 462 | 470 | 2.8421 | 72 | 1
470 | 463 | 471 | 2.6359 | 72 | 1
471 | 464 | 472 | 0.77806 | 75 | 1
472 | 465 | 473 | 0.26134 | 75 | 1
473 | 466 | 474 | 16.9012 | 72 | 1
474 | 467 | 475 | 11.588 | 74 | 1
475 | 467 | 476 | 11.588 | 74 | 1
476 | 470 | 477 | 1.5497 | 72 | 1
477 | 471 | 478 | 1.8521 | 72 | 1
478 | 472 | 479 | 0.87653 | 75 | 1
479 | 473 | 480 | 0.33767 | 75 | 1
480 | 474 | 481 | 1.0024 | 72 | 1
481 | 475 | 482 | 24.516 | 74 | 1
482 | 475 | 483 | 24.516 | 74 | 1
483 | 475 | 484 | 54.2619 | 72 | 1
484 | 477 | 485 | 1.0498 | 72 | 1
485 | 478 | 486 | 0.88493 | 72 | 1
486 | 479 | 487 | 0.9259 | 75 | 1
487 | 480 | 488 | 0.5894 | 75 | 1
488 | 481 | 489 | 0.90446 | 72 | 1
489 | 482 | 490 | 35.1373 | 74 | 1
490 | 482 | 491 | 35.1373 | 74 | 1
491 | 484 | 492 | 3.0516 | 72 | 1
492 | 484 | 493 | 21.5033 | 72 | 1
493 | 485 | 494 | 1.5946 | 72 | 1
494 | 486 | 495 | 0.56058 | 72 | 1
495 | 487 | 496 | 2.0245 | 75 | 1
496 | 488 | 497 | 0.73772 | 75 | 1
497 | 489 | 498 | 1.2293 | 72 | 1
498 | 490 | 499 | 21.4431 | 74 | 1
499 | 490 | 500 | 21.4431 | 74 | 1
500 | 492 | 501 | 1.2898 | 72 | 1
501 | 493 | 502 | 13.7596 | 72 | 1
502 | 494 | 503 | 2.42 | 72 | 1
503 | 495 | 504 | 0.37902 | 72 | 1
504 | 496 | 505 | 45.9153 | 75 | 1
505 | 497 | 506 | 0.50776 | 75 | 1
506 | 498 | 507 | 1.6138 | 72 | 1
507 | 499 | 508 | 3.6927 | 74 | 1
508 | 499 | 509 | 3.6927 | 74 | 1
509 | 501 | 510 | 0.75789 | 72 | 1
510 | 503 | 511 | 1.7169 | 72 | 1
511 | 504 | 512 | 0.52869 | 72 | 1
512 | 505 | 513 | 29.3821 | 72 | 1
513 | 505 | 514 | 7.0588 | 75 | 1
514 | 506 | 515 | 0.4514 | 75 | 1
515 | 508 | 516 | 9.9565 | 74 | 1
516 | 508 | 517 | 9.9565 | 74 | 1
517 | 508 | 518 | 24.9828 | 72 | 1
518 | 510 | 519 | 0.69749 | 72 | 1
519 | 511 | 520 | 1.173 | 72 | 1
520 | 512 | 521 | 0.4035 | 72 | 1
521 | 513 | 522 | 25.911 | 72 | 1
522 | 514 | 523 | 3.808 | 75 | 1
523 | 515 | 524 | 0.3515 | 75 | 1
524 | 516 | 525 | 7.3292 | 74 | 1
525 | 516 | 526 | 7.3292 | 74 | 1
526 | 518 | 527 | 14.7628 | 72 | 1
527 | 519 | 528 | 0.6214 | 72 | 1
528 | 520 | 529 | 0.9269 | 72 | 1
529 | 521 | 530 | 2.8794 | 72 | 1
530 | 523 | 531 | 0.56871 | 75 | 1
531 | 524 | 532 | 0.32104 | 75 | 1
532 | 525 | 533 | 9.9786 | 74 | 1
533 | 525 | 534 | 9.9786 | 74 | 1
534 | 527 | 535 | 11.6973 | 72 | 1
535 | 528 | 536 | 0.64463 | 72 | 1
536 | 529 | 537 | 2.9719 | 72 | 1
537 | 530 | 538 | 10.1518 | 72 | 1
538 | 530 | 539 | 29.4819 | 72 | 1
539 | 531 | 540 | 0.43412 | 75 | 1
540 | 532 | 541 | 0.34591 | 75 | 1
541 | 533 | 542 | 7.0615 | 74 | 1
542 | 533 | 543 | 7.0615 | 74 | 1
543 | 535 | 544 | 4.8334 | 72 | 1
544 | 536 | 545 | 1.946 | 72 | 1
545 | 537 | 546 | 24.0382 | 72 | 1
546 | 538 | 547 | 11.2099 | 72 | 1
547 | 540 | 548 | 0.40601 | 75 | 1
548 | 541 | 549 | 0.45484 | 75 | 1
549 | 542 | 550 | 19.7477 | 74 | 1
550 | 542 | 551 | 19.7477 | 74 | 1
551 | 544 | 552 | 1.5208 | 72 | 1
552 | 544 | 553 | 20.0059 | 72 | 1
553 | 545 | 554 | 1.9611 | 72 | 1
554 | 546 | 555 | 1.1971 | 72 | 1
555 | 547 | 556 | 30.3853 | 72 | 1
556 | 548 | 557 | 0.43296 | 75 | 1
557 | 549 | 558 | 0.32531 | 75 | 1
558 | 550 | 559 | 14.2993 | 74 | 1
559 | 550 | 560 | 14.2993 | 74 | 1
560 | 552 | 561 | 0.55963 | 72 | 1
561 | 553 | 562 | 15.1346 | 72 | 1
562 | 554 | 563 | 18.3242 | 72 | 1
563 | 555 | 564 | 0.94454 | 72 | 1
564 | 557 | 565 | 0.38312 | 75 | 1
565 | 558 | 566 | 0.63471 | 75 | 1
566 | 559 | 567 | 3.1716 | 74 | 1
567 | 559 | 568 | 3.1716 | 74 | 1
568 | 559 | 569 | 20.3184 | 72 | 1
569 | 561 | 570 | 0.8336 | 72 | 1
570 | 564 | 571 | 1.0678 | 72 | 1
571 | 565 | 572 | 0.39186 | 75 | 1
572 | 567 | 573 | 0.75097 | 74 | 1
573 | 567 | 574 | 0.75097 | 74 | 1
574 | 569 | 575 | 2.5686 | 72 | 1
575 | 570 | 576 | 0.5016 | 72 | 1
576 | 571 | 577 | 0.9504 | 72 | 1
577 | 572 | 578 | 2.0225 | 75 | 1
578 | 573 | 579 | 20.3586 | 74 | 1
579 | 573 | 580 | 20.3586 | 74 | 1
580 | 573 | 581 | 1.6885 | 74 | 1
581 | 575 | 582 | 1.8955 | 72 | 1
582 | 576 | 583 | 0.60524 | 72 | 1
583 | 577 | 584 | 1.0939 | 72 | 1
584 | 578 | 585 | 24.9838 | 72 | 1
585 | 578 | 586 | 4.3625 | 75 | 1
586 | 579 | 587 | 14.2676 | 74 | 1
587 | 579 | 588 | 14.2676 | 74 | 1
588 | 581 | 589 | 0.61396 | 74 | 1
589 | 582 | 590 | 1.8443 | 72 | 1
590 | 583 | 591 | 0.53143 | 72 | 1
591 | 584 | 592 | 1.1216 | 72 | 1
592 | 585 | 593 | 1.4397 | 72 | 1
593 | 586 | 594 | 20.847 | 75 | 1
594 | 587 | 595 | 28.5869 | 74 | 1
595 | 587 | 596 | 3.3918 | 74 | 1
596 | 589 | 597 | 0.47137 | 74 | 1
597 | 590 | 598 | 17.3247 | 72 | 1
598 | 591 | 599 | 3.4775 | 72 | 1
599 | 592 | 600 | 1.3482 | 72 | 1
600 | 593 | 601 | 0.72309 | 72 | 1
601 | 594 | 602 | 48.4011 | 72 | 1
602 | 594 | 603 | 24.5118 | 75 | 1
603 | 595 | 604 | 25.4934 | 74 | 1
604 | 595 | 605 | 25.4934 | 74 | 1
605 | 595 | 606 | 25.1956 | 74 | 1
606 | 596 | 607 | 61.5868 | 72 | 1
607 | 596 | 608 | 61.5868 | 72 | 1
608 | 597 | 609 | 0.58275 | 74 | 1
609 | 598 | 610 | 8.0631 | 72 | 1
610 | 599 | 611 | 25.6407 | 72 | 1
611 | 600 | 612 | 0.84522 | 72 | 1
612 | 601 | 613 | 0.60635 | 72 | 1
613 | 602 | 614 | 25.5414 | 72 | 1
614 | 603 | 615 | 23.478 | 75 | 1
615 | 604 | 616 | 20.7509 | 71 | 1
616 | 604 | 617 | 16.4144 | 74 | 1
617 | 604 | 618 | 16.4144 | 74 | 1
618 | 607 | 619 | 14.4957 | 72 | 1
619 | 609 | 620 | 0.33602 | 74 | 1
620 | 610 | 621 | 3.7843 | 72 | 1
621 | 612 | 622 | 3.6325 | 72 | 1
622 | 613 | 623 | 0.49446 | 72 | 1
623 | 615 | 624 | 8.618 | 72 | 1
624 | 615 | 625 | 6.6058 | 75 | 1
625 | 616 | 626 | 28.2675 | 71 | 1
626 | 620 | 627 | 0.4113 | 74 | 1
627 | 621 | 628 | 2.5242 | 72 | 1
628 | 622 | 629 | 15.3141 | 72 | 1
629 | 623 | 630 | 0.77616 | 72 | 1
630 | 624 | 631 | 2.1132 | 72 | 1
631 | 625 | 632 | 1.5198 | 75 | 1
632 | 626 | 633 | 8.2912 | 71 | 1
633 | 627 | 634 | 0.34478 | 74 | 1
634 | 628 | 635 | 3.859 | 72 | 1
635 | 630 | 636 | 1.8508 | 72 | 1
636 | 631 | 637 | 1.451 | 72 | 1
637 | 632 | 638 | 0.75419 | 75 | 1
638 | 633 | 639 | 27.4422 | 71 | 1
639 | 634 | 640 | 0.36497 | 74 | 1
640 | 635 | 641 | 7.5367 | 72 | 1
641 | 636 | 642 | 1.2804 | 72 | 1
642 | 637 | 643 | 2.0115 | 72 | 1
643 | 638 | 644 | 0.8288 | 75 | 1
644 | 640 | 645 | 0.36217 | 74 | 1
645 | 641 | 646 | 2.0833 | 72 | 1
646 | 642 | 647 | 1.6281 | 72 | 1
647 | 643 | 648 | 4.7698 | 72 | 1
648 | 644 | 649 | 0.95631 | 75 | 1
649 | 645 | 650 | 0.49623 | 74 | 1
650 | 646 | 651 | 0.60482 | 72 | 1
651 | 647 | 652 | 0.98905 | 72 | 1
652 | 648 | 653 | 3.6258 | 72 | 1
653 | 649 | 654 | 0.96677 | 75 | 1
654 | 650 | 655 | 0.6544 | 74 | 1
655 | 651 | 656 | 0.52466 | 72 | 1
656 | 651 | 657 | 2.7868 | 72 | 1
657 | 652 | 658 | 0.8929 | 72 | 1
658 | 653 | 659 | 2.5453 | 72 | 1
659 | 654 | 660 | 1.0718 | 75 | 1
660 | 655 | 661 | 1.9254 | 74 | 1
661 | 656 | 662 | 0.49104 | 72 | 1
662 | 657 | 663 | 3.6774 | 72 | 1
663 | 658 | 664 | 1.5059 | 72 | 1
664 | 659 | 665 | 2.6664 | 72 | 1
665 | 660 | 666 | 1.5586 | 75 | 1
666 | 661 | 667 | 1.3738 | 74 | 1
667 | 662 | 668 | 0.50583 | 72 | 1
668 | 663 | 669 | 15.2776 | 72 | 1
669 | 664 | 670 | 1.4805 | 72 | 1
670 | 665 | 671 | 2.1891 | 72 | 1
671 | 666 | 672 | 2.5349 | 72 | 1
672 | 666 | 673 | 4.2853 | 75 | 1
673 | 667 | 674 | 1.0657 | 74 | 1
674 | 668 | 675 | 3.6573 | 72 | 1
675 | 669 | 676 | 6.488 | 72 | 1
676 | 670 | 677 | 0.7005 | 72 | 1
677 | 671 | 678 | 3.6246 | 72 | 1
678 | 672 | 679 | 1.5222 | 72 | 1
679 | 673 | 680 | 27.1354 | 75 | 1
680 | 674 | 681 | 2.1253 | 74 | 1
681 | 675 | 682 | 26.6328 | 72 | 1
682 | 677 | 683 | 0.7694 | 72 | 1
683 | 678 | 684 | 11.7137 | 72 | 1
684 | 679 | 685 | 1.4121 | 72 | 1
685 | 680 | 686 | 19.4235 | 75 | 1
686 | 683 | 687 | 0.73846 | 72 | 1
687 | 684 | 688 | 27.3704 | 72 | 1
688 | 685 | 689 | 1.3778 | 72 | 1
689 | 686 | 690 | 43.0029 | 72 | 1
690 | 686 | 691 | 55.574 | 75 | 1
691 | 687 | 692 | 0.89058 | 72 | 1
692 | 689 | 693 | 1.0335 | 72 | 1
693 | 690 | 694 | 4.0211 | 72 | 1
694 | 690 | 695 | 11.2258 | 72 | 1
695 | 691 | 696 | 50.0633 | 72 | 1
696 | 691 | 697 | 11.5669 | 75 | 1
697 | 692 | 698 | 1.4206 | 72 | 1
698 | 693 | 699 | 1.6417 | 72 | 1
699 | 694 | 700 | 1.2582 | 72 | 1
700 | 695 | 701 | 22.8687 | 72 | 1
701 | 696 | 702 | 29.003 | 72 | 1
702 | 697 | 703 | 12.672 | 74 | 1
703 | 698 | 704 | 3.888 | 72 | 1
704 | 699 | 705 | 2.768 | 72 | 1
705 | 700 | 706 | 0.809 | 72 | 1
706 | 703 | 707 | 33.4265 | 74 | 1
707 | 703 | 708 | 0.58777 | 74 | 1
708 | 704 | 709 | 5.1742 | 72 | 1
709 | 705 | 710 | 20.7403 | 72 | 1
710 | 706 | 711 | 0.48797 | 72 | 1
711 | 707 | 712 | 39.6131 | 74 | 1
712 | 707 | 713 | 20.8285 | 72 | 1
713 | 708 | 714 | 0.55303 | 74 | 1
714 | 709 | 715 | 0.49282 | 72 | 1
715 | 710 | 716 | 17.0148 | 72 | 1
716 | 711 | 717 | 0.49319 | 72 | 1
717 | 712 | 718 | 40.8851 | 74 | 1
718 | 713 | 719 | 2.2297 | 72 | 1
719 | 714 | 720 | 0.51216 | 74 | 1
720 | 715 | 721 | 0.38975 | 72 | 1
721 | 716 | 722 | 5.3909 | 72 | 1
722 | 717 | 723 | 0.44053 | 72 | 1
723 | 718 | 724 | 17.1784 | 74 | 1
724 | 718 | 725 | 49.3547 | 72 | 1
725 | 719 | 726 | 0.85135 | 72 | 1
726 | 720 | 727 | 0.57958 | 74 | 1
727 | 721 | 728 | 0.37854 | 72 | 1
728 | 722 | 729 | 4.9077 | 72 | 1
729 | 723 | 730 | 0.49632 | 72 | 1
730 | 724 | 731 | 23.3428 | 74 | 1
731 | 725 | 732 | 6.6206 | 72 | 1
732 | 726 | 733 | 0.90055 | 72 | 1
733 | 727 | 734 | 0.47461 | 74 | 1
734 | 728 | 735 | 0.40546 | 72 | 1
735 | 729 | 736 | 2.673 | 72 | 1
736 | 730 | 737 | 0.39765 | 72 | 1
737 | 731 | 738 | 27.3297 | 74 | 1
738 | 732 | 739 | 3.4783 | 72 | 1
739 | 733 | 740 | 0.74738 | 72 | 1
740 | 734 | 741 | 0.72658 | 74 | 1
741 | 735 | 742 | 0.37488 | 72 | 1
742 | 736 | 743 | 2.1348 | 72 | 1
743 | 737 | 744 | 0.47698 | 72 | 1
744 | 738 | 745 | 21.9447 | 74 | 1
745 | 739 | 746 | 19.7403 | 72 | 1
746 | 739 | 747 | 0.64426 | 72 | 1
747 | 740 | 748 | 0.88508 | 72 | 1
748 | 741 | 749 | 0.86734 | 74 | 1
749 | 742 | 750 | 0.35328 | 72 | 1
750 | 743 | 751 | 1.8204 | 72 | 1
751 | 744 | 752 | 0.51401 | 72 | 1
752 | 745 | 753 | 8.1491 | 74 | 1
753 | 745 | 754 | 31.2718 | 72 | 1
754 | 746 | 755 | 16.0464 | 72 | 1
755 | 747 | 756 | 0.4659 | 72 | 1
756 | 748 | 757 | 0.86317 | 72 | 1
757 | 749 | 758 | 0.65757 | 74 | 1
758 | 750 | 759 | 0.49135 | 72 | 1
759 | 751 | 760 | 2.1362 | 72 | 1
760 | 752 | 761 | 0.93778 | 72 | 1
761 | 753 | 762 | 11.2353 | 74 | 1
762 | 754 | 763 | 26.1391 | 72 | 1
763 | 756 | 764 | 0.39317 | 72 | 1
764 | 757 | 765 | 1.1867 | 72 | 1
765 | 758 | 766 | 0.64242 | 74 | 1
766 | 759 | 767 | 0.60213 | 72 | 1
767 | 760 | 768 | 1.952 | 72 | 1
768 | 761 | 769 | 7.016 | 72 | 1
769 | 762 | 770 | 27.6391 | 74 | 1
770 | 763 | 771 | 19.0116 | 72 | 1
771 | 763 | 772 | 0.6884 | 72 | 1
772 | 764 | 773 | 0.66412 | 72 | 1
773 | 765 | 774 | 1.6325 | 72 | 1
774 | 766 | 775 | 0.41876 | 74 | 1
775 | 767 | 776 | 2.8539 | 72 | 1
776 | 768 | 777 | 3.0282 | 72 | 1
777 | 769 | 778 | 21.5006 | 72 | 1
778 | 770 | 779 | 22.4019 | 74 | 1
779 | 771 | 780 | 18.6294 | 72 | 1
780 | 772 | 781 | 0.6582 | 72 | 1
781 | 773 | 782 | 0.93002 | 72 | 1
782 | 774 | 783 | 1.7276 | 72 | 1
783 | 775 | 784 | 0.51216 | 74 | 1
784 | 776 | 785 | 24.402 | 72 | 1
785 | 777 | 786 | 6.1137 | 72 | 1
786 | 779 | 787 | 17.5042 | 74 | 1
787 | 781 | 788 | 0.70958 | 72 | 1
788 | 782 | 789 | 0.69009 | 72 | 1
789 | 783 | 790 | 1.1476 | 72 | 1
790 | 784 | 791 | 0.48567 | 74 | 1
791 | 786 | 792 | 1.8262 | 72 | 1
792 | 786 | 793 | 10.8873 | 72 | 1
793 | 787 | 794 | 15.8204 | 74 | 1
794 | 788 | 795 | 0.6336 | 72 | 1
795 | 789 | 796 | 1.1432 | 72 | 1
796 | 790 | 797 | 1.168 | 72 | 1
797 | 791 | 798 | 0.48421 | 74 | 1
798 | 792 | 799 | 1.5927 | 72 | 1
799 | 793 | 800 | 17.4213 | 72 | 1
800 | 794 | 801 | 1.0853 | 72 | 1
801 | 794 | 802 | 14.8003 | 79 | 1
802 | 795 | 803 | 0.6997 | 72 | 1
803 | 796 | 804 | 7.9348 | 72 | 1
804 | 797 | 805 | 0.55846 | 72 | 1
805 | 798 | 806 | 0.65002 | 74 | 1
806 | 799 | 807 | 1.3172 | 72 | 1
807 | 800 | 808 | 14.8848 | 72 | 1
808 | 801 | 809 | 1.0882 | 72 | 1
809 | 802 | 810 | 16.2354 | 74 | 1
810 | 802 | 811 | 16.2354 | 74 | 1
811 | 803 | 812 | 0.45112 | 72 | 1
812 | 804 | 813 | 17.5269 | 72 | 1
813 | 805 | 814 | 0.88831 | 72 | 1
814 | 806 | 815 | 2.2221 | 74 | 1
815 | 807 | 816 | 1.0243 | 72 | 1
816 | 808 | 817 | 8.4242 | 72 | 1
817 | 809 | 818 | 1.0903 | 72 | 1
818 | 810 | 819 | 13.6129 | 74 | 1
819 | 810 | 820 | 13.6129 | 74 | 1
820 | 812 | 821 | 0.69289 | 72 | 1
821 | 814 | 822 | 0.83392 | 72 | 1
822 | 815 | 823 | 2.5688 | 74 | 1
823 | 816 | 824 | 1.0418 | 72 | 1
824 | 818 | 825 | 1.0837 | 72 | 1
825 | 819 | 826 | 14.6335 | 74 | 1
826 | 819 | 827 | 14.6335 | 74 | 1
827 | 821 | 828 | 5.6992 | 72 | 1
828 | 822 | 829 | 1.1915 | 72 | 1
829 | 823 | 830 | 2.622 | 74 | 1
830 | 824 | 831 | 0.90409 | 72 | 1
831 | 825 | 832 | 1.0878 | 72 | 1
832 | 826 | 833 | 12.0146 | 74 | 1
833 | 826 | 834 | 12.0146 | 74 | 1
834 | 828 | 835 | 19.6421 | 72 | 1
835 | 829 | 836 | 12.5775 | 72 | 1
836 | 831 | 837 | 0.64933 | 72 | 1
837 | 832 | 838 | 1.087 | 72 | 1
838 | 833 | 839 | 12.899 | 74 | 1
839 | 833 | 840 | 12.899 | 74 | 1
840 | 836 | 841 | 5.0307 | 72 | 1
841 | 837 | 842 | 0.75388 | 72 | 1
842 | 838 | 843 | 1.0877 | 72 | 1
843 | 839 | 844 | 25.3925 | 71 | 1
844 | 839 | 845 | 19.1199 | 74 | 1
845 | 839 | 846 | 19.1199 | 74 | 1
846 | 841 | 847 | 2.5546 | 72 | 1
847 | 842 | 848 | 1.1357 | 72 | 1
848 | 843 | 849 | 0.53096 | 72 | 1
849 | 844 | 850 | 3.715 | 71 | 1
850 | 845 | 851 | 23.0419 | 74 | 1
851 | 845 | 852 | 23.0419 | 74 | 1
852 | 847 | 853 | 0.56528 | 72 | 1
853 | 848 | 854 | 1.8555 | 72 | 1
854 | 849 | 855 | 11.9333 | 72 | 1
855 | 850 | 856 | 10.466 | 71 | 1
856 | 851 | 857 | 36.2318 | 74 | 1
857 | 851 | 858 | 36.2318 | 74 | 1
858 | 853 | 859 | 0.44518 | 72 | 1
859 | 854 | 860 | 14.8896 | 72 | 1
860 | 854 | 861 | 39.648 | 72 | 1
861 | 855 | 862 | 7.76 | 72 | 1
862 | 856 | 863 | 12.2897 | 71 | 1
863 | 857 | 864 | 14.7248 | 74 | 1
864 | 857 | 865 | 14.7248 | 74 | 1
865 | 859 | 866 | 0.47698 | 72 | 1
866 | 862 | 867 | 6.7869 | 72 | 1
867 | 863 | 868 | 1.5942 | 71 | 1
868 | 864 | 869 | 9.1729 | 74 | 1
869 | 864 | 870 | 9.1729 | 74 | 1
870 | 866 | 871 | 0.38162 | 72 | 1
871 | 867 | 872 | 7.119 | 72 | 1
872 | 868 | 873 | 2.0039 | 71 | 1
873 | 868 | 874 | 4.4584 | 71 | 1
874 | 869 | 875 | 6.336 | 74 | 1
875 | 869 | 876 | 6.336 | 74 | 1
876 | 871 | 877 | 0.37054 | 72 | 1
877 | 872 | 878 | 12.1556 | 72 | 1
878 | 873 | 879 | 1.8542 | 71 | 1
879 | 874 | 880 | 10.4338 | 71 | 1
880 | 875 | 881 | 5.3391 | 74 | 1
881 | 875 | 882 | 5.3391 | 74 | 1
882 | 877 | 883 | 0.3696 | 72 | 1
883 | 878 | 884 | 2.9815 | 72 | 1
884 | 879 | 885 | 2.8195 | 71 | 1
885 | 880 | 886 | 24.7521 | 71 | 1
886 | 883 | 887 | 0.36527 | 72 | 1
887 | 884 | 888 | 3.2891 | 72 | 1
888 | 884 | 889 | 16.671 | 73 | 1
889 | 885 | 890 | 3.5631 | 71 | 1
890 | 887 | 891 | 6.5319 | 72 | 1
891 | 888 | 892 | 5.4004 | 72 | 1
892 | 889 | 893 | 14.1393 | 73 | 1
893 | 890 | 894 | 13.8711 | 71 | 1
894 | 891 | 895 | 30.7554 | 72 | 1
895 | 891 | 896 | 17.2059 | 72 | 1
896 | 892 | 897 | 1.0678 | 72 | 1
897 | 893 | 898 | 23.7652 | 73 | 1
898 | 894 | 899 | 25.1977 | 71 | 1
899 | 895 | 900 | 20.4251 | 72 | 1
900 | 897 | 901 | 0.90224 | 72 | 1
901 | 901 | 902 | 0.76032 | 72 | 1
902 | 902 | 903 | 0.98905 | 72 | 1
903 | 903 | 904 | 1.79 | 72 | 1
904 | 904 | 905 | 3.1036 | 72 | 1
905 | 905 | 906 | 25.4216 | 72 | 1
999 | 1000 | 1001 | 5280 | 100 | 1

## Transformers
TrfNo | TrfName | FromNode | ToNode | kVA | FNodekV | FromType | TNodekV | ToType | R% | X% | Status | kVAtype | kVA1 | kVA2 | kVA3 | r1% | x1% | r2% | x2% | r3% | x3% | Ng
950 | TR1 | 1001 | 1 | 800 | 11 | 0 | 0.416 | 2 | 0.4 | 4 | 1 | 0 | 800 | 800 | 800 | 0.4 | 4 | 0.4 | 4 | 0.4 | 4 | 0
Note on G1: Author: 0- Delta 1- WYE Ungrounded 2- WYE Grounded
Note on I1: Author: 0- Delta 1- WYE Ungrounded 2- WYE Grounded
Note on L1: Author: 0- Out of service 1- In service
Note on M1: Author: Flag 0- Trf as a single Three-phase unit Transformer. Flag 1- Three individual Transformers for each phase. Flag 3 - using User-Defined Transformer Library
Note on W1: Author: Neutral ground resistance

## Loads
Node | Load_Type | Load_Model | Ph-1_kW | Ph-1_kVAr | Ph-2_kW | Ph-2_kVAr | Ph-3_kW | Ph-3_kVAr | Ph1_flg | Ph2_flg | Ph3_flg | load_data | Status
34 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
47 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
70 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
73 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
74 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
83 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
178 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
208 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
225 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
248 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
249 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
264 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
276 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
289 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
314 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
320 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
327 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
337 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
342 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
349 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
387 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
388 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
406 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
458 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
502 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
522 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
539 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
556 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
562 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
563 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
611 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
614 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
619 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
629 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
639 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
676 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
682 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
688 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
701 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
702 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
755 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
778 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
780 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
785 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
813 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
817 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
835 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 0 | 1 | 1 | 1
860 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
861 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
886 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
896 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
898 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
899 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 0 | 1 | 0 | 1 | 1
900 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
906 | 1 | 0 | 1 | 0.95 | 1 | 0.95 | 1 | 0.95 | 1 | 0 | 0 | 1 | 1
Note on B1: Author: 0- Delta 1- Star
Note on C1: Author: 0 - PQ load 1 - Const Current 2 - Const Z
Note on M1: Author: 0- kW & kVAr 1- KW & pf 2- kVA & pf
Note on N1: Author: 1- Inservice 0-out of service

## Caps
Node | Cap Type | Cap Model | kVLN | Ph1_kW | Ph1_kVAr | Ph2_kW | Ph2_kVAr | Ph3_kW | Ph3_kVAr | Status | CapControl | EachBank | Ph1 | Ph2 | Ph3
10 | 1 | 0 | 2.4018 | 0 | 200 | 0 | 200 | 0 | 200 | 0 | 1 | 20 | 10 | 10 | 10
Note on B1: Author: 0- Delta 1- Star
Note on C1: Author: 0 - Three Phase 1 - Two Phase 2 - Single Phase
Note on E1: Author: 0 - no loss
Note on L1: 0-Fixed capacitor, rated kVAR entered in CapsD(6,8,10) 1- based on taps, taps on Ph1 times each bank capacity

## Regulator
Regulator ID | From Node | To Node | Location | Regulated mode | Type | Configuration | Monitoring Phase | Bandwidth: | PT Ratio | Primary CT Rating | Vmin | Vmax | No of Steps | Tap A | Tap B | Tap C | Tap setting | Compensator Settings a | Compensator Settings b | Compensator Settings c | R - Setting | X - Setting | R - Setting | X - Setting | R - Setting | X - Setting | Voltage Level | status | CTs
0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 20 | 700 | 120 | 122 | 40 | 10 | 8 | 11 | 0 | 0 | 0 | 0 | 3 | 9 | 3 | 9 | 3 | 9 | 122 | 0 | 0
Note on D1: Author: bus no from which the bus voltage is extracted 0 - from bus 1- To bus
Note on E1: Author: 1- To bus mode 2- Based on r x setting
Note on F1: Author: 0-Type A 1- Type B
Note on G1: Author: 0- single 1- three phase 2- open delta (not modeled)
Note on H1: Author: Not used
Note on R1: Author: 0- Tap settings are forced 1- Tap settings are free to change 2- tap settings are forced but allow during optimization
Note on S1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on T1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on U1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on AC1: Author: 0- in service 1- by pass 2 - out of service (open in ckt)

## Cable
No | Phase Cond. | Diameter over Insulation (inch) | Diameter overScreen (inch) | Outside Diameter (inch)/Jacket Thickness (mils) | Copper 1/3 Neutral / Outside Diameter (inch) | Ampacity | Type
1 | 2 (7x) | 0.78 | 0.85 | 0.98 | 6 x 14 | 135 | 0
2 | 1/0 (19x) | 0.85 | 0.93 | 1.06 | 6 x 14 | 175 | 0
3 | 2/0 (19x) | 0.9 | 0.97 | 1.1 | 7 x 14 | 200 | 0
4 | 250 (37x) | 1.06 | 1.16 | 1.29 | 13 x 14 | 260 | 0
5 | 500 (37x) | 1.29 | 1.39 | 1.56 | 16 x 12 | 385 | 0
6 | 1000 (61x) | 1.64 | 1.77 | 1.98 | 20 x 10 | 550 | 0
7 | 1/0 AL | 0.82 | 0.88 | 80 | 1.06 | 165 | 1
Note on A1: Concentric Neutral 15 kV All Aluminum (AA) Cable - 1/3 Neutral Tape Shielded 15 kV All Aluminum (AA) Cable - Tape Thickness = 5 mils

## UDB_trafo
Config. | R11 | X11 | R12 | X12 | R13 | X13 | R22 | X22 | R23 | X23 | R33 | X33
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4884 | 11.1975
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46794 | 2.1057

## UDB_Line
Config. | R11 | X11 | R12 | X12 | R13 | X13 | R22 | X22 | R23 | X23 | R33 | X33 | Y11 | Y12 | Y13 | Y22 | Y23 | Y33 | Name
70 | 3.97 | 0.099 | 0 | 0 | -2.2204e-16 | 0 | 3.97 | 0.099 | 0 | 6.6613e-16 | 3.97 | 0.099 | 0 | 0 | 0 | 0 | 0 | 0 | 2c_.007
71 | 1.257 | 0.085 | 2.7756e-17 | 5.5511e-17 | -2.7756e-17 | 5.5511e-17 | 1.257 | 0.085 | -5.5511e-17 | 1.6653e-16 | 1.257 | 0.085 | 0 | 0 | 0 | 0 | 0 | 0 | 2c_.0225
72 | 1.1667 | 0.088 | 0.016667 | 0 | 0.016667 | 0 | 1.1667 | 0.088 | 0.016667 | 1.6653e-16 | 1.1667 | 0.088 | 0 | 0 | 0 | 0 | 0 | 0 | 2c_16
73 | 0.832 | 0.092 | -0.036001 | -5.5511e-17 | -0.036001 | -5.5511e-17 | 0.832 | 0.092 | -0.036001 | 1.6653e-16 | 0.832 | 0.092 | 0 | 0 | 0 | 0 | 0 | 0 | 35_SAC_XSC
74 | 0.83966 | 0.080333 | 0.37067 | 0.0053334 | 0.37067 | 0.0053334 | 0.83967 | 0.080333 | 0.37067 | 0.0053334 | 0.83967 | 0.080333 | 0 | 0 | 0 | 0 | 0 | 0 | 4c_.06
75 | 0.50233 | 0.075 | 0.22834 | 0.002 | 0.22834 | 0.002 | 0.50234 | 0.075 | 0.22834 | 0.002 | 0.50234 | 0.075 | 0 | 0 | 0 | 0 | 0 | 0 | 4c_.1
76 | 0.16566 | 0.070333 | 0.076668 | 0.0028334 | 0.076668 | 0.0028334 | 0.16567 | 0.070333 | 0.076668 | 0.0028334 | 0.16567 | 0.070333 | 0 | 0 | 0 | 0 | 0 | 0 | 4c_.35
77 | 0.304 | 0.071333 | 0.138 | 0.0033334 | 0.138 | 0.0033334 | 0.304 | 0.071333 | 0.138 | 0.0033334 | 0.304 | 0.071333 | 0 | 0 | 0 | 0 | 0 | 0 | 4c_185
78 | 0.79899 | 0.075 | 0.35301 | 0.0040001 | 0.35301 | 0.0040001 | 0.79901 | 0.075 | 0.35301 | 0.0040001 | 0.79901 | 0.075 | 0 | 0 | 0 | 0 | 0 | 0 | 4c_70
79 | 0.48266 | 0.080333 | 0.16067 | 0.0063334 | 0.16067 | 0.0063334 | 0.48267 | 0.080333 | 0.16067 | 0.0063334 | 0.48267 | 0.080333 | 0 | 0 | 0 | 0 | 0 | 0 | 4c_95_SAC_XC
100 | 2.219e-13 | 1334.6579 | 0 | 1332.4938 | -2.2193e-13 | 1332.4938 | 1.1102e-16 | 1334.7166 | -2.2238e-13 | 1332.4938 | -2.2186e-13 | 1334.7166 | 0 | 0 | 0 | 0 | 0 | 0 | SRC_Equiv
101 | 0 | 1271.1181 | 0 | 1269.0011 | 0 | 1269.0011 | 0 | 1271.1181 | 0 | 1269.0011 | 0 | 1271.1181 | 0 | 0 | 0 | 0 | 0 | 0 | SRC_Equiv105

## Configuration
No | Config | Phasing | Cable | SpacingID | PhA_ cond | PhB_ cond | PhC_ cond | Neu_Cond | Type | n | Outside diameter (Dod) | No of strands(k) (cable only!) | Relative permittivity (Cable!) | 1_flag | 2_flag | 3_flag | Neu_Flag_1 | Neu_Flag_2 | Neu_Flag_3 | dis Cable and neutral
1 | 1 | BACN | 601 | 1 | 2 | 2 | 2 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
2 | 2 | C A B N | 602 | 2 | 6 | 6 | 6 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
3 | 3 | CBN | 603 | 3 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 0 | 1 | 1 | 1 | 0 | 0
4 | 4 | CAN | 604 | 4 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 1 | 0 | 1 | 1 | 0 | 0
5 | 5 | CN | 605 | 5 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 0 | 0 | 1 | 1 | 0 | 0
6 | 6 | ABCN UG | 606 | 6 | 4 | 4 | 4 | 15 | 1 | 6 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 1 | 1
7 | 7 | AN UG TS | 607 | - | 16 | - | - | 9 | 2 | 3 | 0.88 | 5 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0.08333
8 | 8 | ABCN UG | 721 | 6 | 1 | 1 | 1 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
9 | 9 | ABCN UG | 722 | 6 | 3 | 3 | 3 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
10 | 10 | ABCN UG | 723 | 6 | 7 | 7 | 7 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
11 | 11 | ABCN UG | 724 | 6 | 10 | 10 | 10 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
12 | 12 | BACN | 300 | 1 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
13 | 13 | BACN | 301 | 1 | 11 | 11 | 11 | 11 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
14 | 14 | AN OH | 302 | 8 | 12 | 12 | 12 | 12 | 0 | 3 | 1.29 | 13 |  | 1 | 0 | 0 | 1 | 0 | 0
15 | 15 | BN OH | 303 | 9 | 12 | 12 | 12 | 12 | 0 | 3 | 1.29 | 13 |  | 0 | 1 | 0 | 1 | 0 | 0
16 | 16 | BN OH | 304 | 9 | 11 | 11 | 11 | 11 | 0 | 3 | 1.29 | 13 |  | 0 | 1 | 0 | 1 | 0 | 0
17 | 17 | ABC N OHL | 708 | 10 | 5 | 5 | 5 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
18 | 18 | ABC N OHL | 708 | 11 | 5 | 5 | 5 | 6 | 0 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
Note on J1: Author: 0 - OH Lines 1 - Concentric Neutral Cable 2 - Tape Shielded Cable
Note on K1: Author: Primitive size of Matrix

## Conductortype
No | Conductor | Type | Res. (Ohms/mi) | Dia. (Inch) | GMR (Ft) | Rating (Amps)
1 | 1,000,000 CM | AA | 0.105 | 1.15 | 0.0368 | 698
2 | 556,500 CM | ACSR | 0.186 | 0.927 | 0.0311 | 730
3 | 500,000 CM | AA | 0.206 | 0.813 | 0.026 | 483
4 | 250,000 CM | AA | 0.41 | 0.567 | 0.0171 | 329
5 | 336,400 CM | ACSR | 0.306 | 0.721 | 0.0244 | 530
6 | #4/0 | ACSR | 0.592 | 0.563 | 0.00814 | 340
7 | #2/0 | AA | 0.769 | 0.414 | 0.0125 | 230
8 | #1/0 | ACSR | 1.12 | 0.398 | 0.00446 | 230
9 | #1/0 | CU | 0.607 | 0.368 | 0.01113 | 310
10 | #2 | AA | 1.54 | 0.292 | 0.00883 | 156
11 | #2 | ACSR | 1.69 | 0.316 | 0.00418 | 180
12 | #4 | ACSR | 2.55 | 0.257 | 0.00452 | 140
13 | #10 | CU | 5.903 | 0.102 | 0.00331 | 80
14 | #12 | CU | 9.375 | 0.081 | 0.00262 | 75
15 | #14 | CU | 14.872 | 0.064 | 0.00208 | 20
16 | #1/0 | AA | 0.97 | 0.368 | 0.0111 | 202
17 | #4 | ACSR | 2.57 | 0.25 | 0.00437 | 140

## Spacing
SI No | Spacing No | n | X-PhaseCond1 | Y-PhaseCond2 | X-PhaseCond2 | Y-PhaseCond2 | X-PhaseCond3 | Y-PhaseCond3 | X-Neutral1 | Y-Neutral1 | X-Neutral2 | Y-Neutral2 | X-Neutral3 | Y-Neutral3
1 | 1 | 4 | 2.5 | 28 | 0 | 28 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
2 | 2 | 4 | 2.5 | 28 | 7 | 28 | 0 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
3 | 3 | 4 | 9999 | 9999 | 7 | 28 | 0 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
4 | 4 | 4 | 0 | 28 | 9999 | 9999 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
5 | 5 | 4 | 9999 | 9999 | 9999 | 9999 | 0 | 29 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
6 | 6 | 6 | 0 | 0 | 0.5 | 0 | 1 | 0 | 0 | 0.0511 | 0.5 | 0.0511 | 1 | 0.0511 | 515
7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 9999 | 9999 | 9999 | 9999
8 | 8 | 4 | 0 | 29 | 9999 | 9999 | 9999 | 9999 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
9 | 9 | 4 | 9999 | 9999 | 0 | 29 | 9999 | 9999 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
10 | 10 | 4 | 0 | 28 | 2.5 | 28 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
11 | 11 | 4 | 0 | 28 | 2.5 | 28 | 7 | 28 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999