## StudyCase
Case | LF_Method | Tolerance | Iteration limit | Initialization | System Freq | Earth Resistivity | Load | Reference bus | VoltageStart | Source Voltage BFS | AngleRef | Load Voltage Sentivity factor | LoadData
1 | 0 | 0.0001 | 500 | 0 | 60 | 100 | 0 | 650 | 1 | 0 | 0 | 0.75 | 0
Note on E1: hemanth: 0 - Flat Start 1 - Pre defined
Note on G1: Author: earth sentivity for computing the line impedance using carson's eq
Note on K1: 0- voltage data reference from db 1- voltage data from online data
Note on N1: Author: 0 - from db 1 - from real time feed (Not available for public)

## Nodes
BusNo | BusName | ZoneNo | Vnom (kVLL) | Vmin | Vmax
60 | Bus60 | 1 | 4.16 | 3.744 | 4.576
632 | Bus632 | 1 | 4.16 | 3.744 | 4.576
633 | Bus633 | 1 | 4.16 | 3.744 | 4.576
634 | Bus634 | 1 | 0.48 | 0.432 | 0.528
645 | Bus645 | 1 | 4.16 | 3.744 | 4.576
646 | Bus646 | 1 | 4.16 | 3.744 | 4.576
650 | Bus650 | 1 | 4.16 | 3.744 | 4.576
652 | Bus652 | 1 | 4.16 | 3.744 | 4.576
671 | Bus671 | 1 | 4.16 | 3.744 | 4.576
672 | Bus672 | 1 | 4.16 | 3.744 | 4.576
673 | Bus673 | 1 | 4.16 | 3.744 | 4.576
675 | Bus675 | 1 | 4.16 | 3.744 | 4.576
680 | Bus680 | 1 | 4.16 | 3.744 | 4.576
684 | Bus684 | 1 | 4.16 | 3.744 | 4.576
692 | Bus692 | 1 | 4.16 | 3.744 | 4.576
611 | Bus611 | 1 | 4.16 | 3.744 | 4.576

## Branch
BranchNo | FromNode | ToNodeB | Length (ft) | Config | Status
90 | 632 | 645 | 500 | 3 | 1
91 | 632 | 633 | 500 | 2 | 1
93 | 645 | 646 | 300 | 3 | 1
94 | 60 | 632 | 2000 | 1 | 1
95 | 684 | 652 | 800 | 7 | 1
96 | 632 | 673 | 500 | 1 | 1
97 | 671 | 684 | 300 | 4 | 1
98 | 671 | 680 | 1000 | 1 | 1
99 | 671 | 692 | 0.001 | 1 | 1
100 | 684 | 611 | 300 | 5 | 1
101 | 692 | 675 | 500 | 6 | 1
102 | 673 | 672 | 1500 | 1 | 1
103 | 672 | 671 | 0.001 | 1 | 1

## Transformers
TrfNo | TrfName | FromNode | ToNode | kVA | FNodekV | FromType | TNodekV | ToType | R% | X% | Status | kVAtype | kVA1 | kVA2 | kVA3 | r1% | x1% | r2% | x2% | r3% | x3% | Ng
25 | XFM1 | 633 | 634 | 500 | 4.16 | 2 | 0.48 | 2 | 1.1 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on G1: Author: 0- Delta 1- WYE Ungrounded 2- WYE Grounded
Note on I1: Author: 0- Delta 1- WYE Ungrounded 2- WYE Grounded
Note on L1: Author: 0- Out of service 1- In service
Note on M1: Author: Flag 0- Trf as a single Three-phase unit Transformer. Flag 1- Three individual Transformers for each phase. Flag 3 - using User-Defined Transformer Library
Note on W1: Author: Neutral ground resistance

## Loads
Node | Load_Type | Load_Model | Ph-1_kW | Ph-1_kVAr | Ph-2_kW | Ph-2_kVAr | Ph-3_kW | Ph-3_kVAr | Ph1_flg | Ph2_flg | Ph3_flg | load_data | Status
634 | 1 | 0 | 160 | 110 | 120 | 90 | 120 | 90 | 1 | 1 | 1 | 0 | 1
645 | 1 | 0 | 0 | 0 | 170 | 125 | 0 | 0 | 0 | 1 | 0 | 0 | 1
646 | 0 | 2 | 0 | 0 | 230 | 132 | 0 | 0 | 0 | 1 | 0 | 0 | 1
652 | 1 | 2 | 128 | 86 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
671 | 0 | 0 | 385 | 220 | 385 | 220 | 385 | 220 | 1 | 1 | 1 | 0 | 1
675 | 1 | 0 | 485 | 190 | 68 | 60 | 290 | 212 | 1 | 1 | 1 | 0 | 1
692 | 0 | 1 | 0 | 0 | 0 | 0 | 170 | 151 | 0 | 0 | 1 | 0 | 1
611 | 1 | 1 | 0 | 0 | 0 | 0 | 170 | 80 | 0 | 0 | 1 | 0 | 1
672 | 1 | 0 | 5.667 | 3.333 | 22 | 12.667 | 39 | 22.667 | 1 | 1 | 1 | 0 | 1
673 | 1 | 0 | 11.333 | 6.667 | 44 | 25.333 | 78 | 45.333 | 1 | 1 | 1 | 0 | 1
Note on B1: Author: 0- Delta 1- Star
Note on C1: Author: 0 - PQ load 1 - Const Current 2 - Const Z
Note on M1: Author: 0- kW & kVAr 1- KW & pf 2- kVA & pf
Note on N1: Author: 1- Inservice 0-out of service

## Caps
Node | Cap Type | Cap Model | kVLN | Ph1_kW | Ph1_kVAr | Ph2_kW | Ph2_kVAr | Ph3_kW | Ph3_kVAr | Status | CapControl | EachBank | Ph1 | Ph2 | Ph3
675 | 1 | 0 | 2.4018 | 0 | 200 | 0 | 200 | 0 | 200 | 1 | 1 | 20 | 10 | 10 | 10
611 | 1 | 1 | 2.4018 | 0 | 0 | 0 | 0 | 0 | 100 | 1 | 1 | 10 | 0 | 0 | 10
Note on B1: Author: 0- Delta 1- Star
Note on C1: Author: 0 - Three Phase 1 - Two Phase 2 - Single Phase
Note on E1: Author: 0 - no loss
Note on L1: 0-Fixed capacitor, rated kVAR entered in CapsD(6,8,10) 1- based on taps, taps on Ph1 times each bank capacity

## Regulator
Regulator ID | From Node | To Node | Location | Regulated mode | Type | Configuration | Monitoring Phase | Bandwidth: | PT Ratio | Primary CT Rating | Vmin | Vmax | No of Steps | Tap A | Tap B | Tap C | Tap setting | Compensator Settings a | Compensator Settings b | Compensator Settings c | R - Setting | X - Setting | R - Setting | X - Setting | R - Setting | X - Setting | Voltage Level | status | CTs
26 | 650 | 60 | 632 | 1 | 1 | 0 | 0 | 2 | 20 | 700 | 120 | 122 | 40 | 10 | 8 | 11 | 0 | 0 | 0 | 0 | 3 | 9 | 3 | 9 | 3 | 9 | 122 | 0 | 0
Note on D1: Author: bus no from which the bus voltage is extracted 0 - from bus 1- To bus
Note on E1: Author: 1- To bus mode 2- Based on r x setting
Note on F1: Author: 0-Type A 1- Type B
Note on G1: Author: 0- single 1- three phase 2- open delta (not modeled)
Note on H1: Author: Not used
Note on R1: Author: 0- Tap settings are forced 1- Tap settings are free to change 2- tap settings are forced but allow during optimization
Note on S1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on T1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on U1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on AC1: Author: 0- in service 1- by pass 2 - out of service (open in ckt)

## Cable
No | Phase Cond. | Diameter over Insulation (inch) | Diameter overScreen (inch) | Outside Diameter (inch)/Jacket Thickness (mils) | Copper 1/3 Neutral / Outside Diameter (inch) | Ampacity | Type
1 | 2 (7x) | 0.78 | 0.85 | 0.98 | 6 x 14 | 135 | 0
2 | 1/0 (19x) | 0.85 | 0.93 | 1.06 | 6 x 14 | 175 | 0
3 | 2/0 (19x) | 0.9 | 0.97 | 1.1 | 7 x 14 | 200 | 0
4 | 250 (37x) | 1.06 | 1.16 | 1.29 | 13 x 14 | 260 | 0
5 | 500 (37x) | 1.29 | 1.39 | 1.56 | 16 x 12 | 385 | 0
6 | 1000 (61x) | 1.64 | 1.77 | 1.98 | 20 x 10 | 550 | 0
7 | 1/0 AL | 0.82 | 0.88 | 80 | 1.06 | 165 | 1
Note on A1: Concentric Neutral 15 kV All Aluminum (AA) Cable - 1/3 Neutral Tape Shielded 15 kV All Aluminum (AA) Cable - Tape Thickness = 5 mils

## UDB_trafo
Config. | R11 | X11 | R12 | X12 | R13 | X13 | R22 | X22 | R23 | X23 | R33 | X33
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4884 | 11.1975
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.46794 | 2.1057

## UDB_Line
Config. | R11 | X11 | R12 | X12 | R13 | X13 | R22 | X22 | R23 | X23 | R33 | X33 | Y11 | Y12 | Y13 | Y22 | Y23 | Y33 | Name
20 | 0.2926 | 0.1973 | 0.0673 | -0.0368 | 0.0337 | -0.0417 | 0.2646 | 0.19 | 0.0673 | -0.0368 | 0.2926 | 0.1973 | 159.7919 | 0 | 0 | 159.7919 | 0 | 159.7919 | 721
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4884 | 11.1975 | 127.8306 | 0 | 0 | 127.8306 | 0 | 127.8306 | 722
22 | 1.2936 | 0.6713 | 0.4871 | 0.2111 | 0.4585 | 0.1521 | 1.3022 | 0.6326 | 0.4871 | 0.2111 | 1.2936 | 0.6713 | 74.8405 | 0 | 0 | 74.8405 | 0 | 74.8405 | 723
23 | 2.0952 | 0.7758 | 0.5204 | 0.2768 | 0.4926 | 0.2123 | 2.1068 | 0.7398 | 0.5204 | 0.2738 | 2.0952 | 0.7758 | 60.248 | 0 | 0 | 60.2483 | 0 | 60.2483 | 724
50 | 0.023205 | 0.029764 | 0 | 0 | 0.0013003 | 0.007994 | 0 | 0 | 0 | 0 | 0.023205 | 0.029764 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0.0088686 | 0.041313 | 0.0020849 | 0.015892 | 0.0020817 | 0.012798 | 0.0042213 | 0.038038 | 0.0020849 | 0.015892 | 0.0088686 | 0.041313 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 0.0044925 | 0.027695 | 0.0016038 | 0.011254 | 0.0016002 | 0.0091507 | 0.0030538 | 0.026276 | 0.0016038 | 0.011254 | 0.0044925 | 0.027695 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 0.002968 | 0.018297 | 0.0010596 | 0.0074352 | 0.0010572 | 0.0060455 | 0.0020175 | 0.017359 | 0.0010596 | 0.0074352 | 0.002968 | 0.018297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 0.003525 | 0.021731 | 0.0012584 | 0.0088305 | 0.0012556 | 0.0071801 | 0.0023962 | 0.020617 | 0.0012584 | 0.0088305 | 0.003525 | 0.021731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 0.0038096 | 0.023486 | 0.00136 | 0.0095434 | 0.001357 | 0.0077598 | 0.0025896 | 0.022282 | 0.00136 | 0.0095434 | 0.0038096 | 0.023486 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 0.0082434 | 0.050819 | 0.0029428 | 0.02065 | 0.0029363 | 0.016791 | 0.0056035 | 0.048214 | 0.0029428 | 0.02065 | 0.0082434 | 0.050819 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 0.00047709 | 0.0030177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 0.00083826 | 0.0053022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0.0048956 | 0.030966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0.0030658 | 0.019392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 0.0030326 | 0.019182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 0.0041132 | 0.026017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 0.0040762 | 0.025783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 0.0052171 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 0.0045126 | 0.028543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0.0044785 | 0.028328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 0.0025655 | 0.00096719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 0.042635 | 0.016073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 0.0061134 | 0.028479 | 0.0014372 | 0.010955 | 0.001435 | 0.008822 | 0.00438 | 0.027418 | 0.0014372 | 0.010955 | 0.0061134 | 0.028479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 0.0010253 | 0.00024582 | 0.00025839 | 6.4829e-05 | 0.00025839 | 6.4829e-05 | 0.0010253 | 0.00024582 | 0.00025839 | 6.4829e-05 | 0.0010253 | 0.00024582 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 0.0081542 | 0.001955 | 0.0020549 | 0.00051557 | 0.0020549 | 0.00051557 | 0.0081542 | 0.001955 | 0.0020549 | 0.00051557 | 0.0081542 | 0.001955 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 0.048493 | 0.013265 | 0.012406 | 0.0011258 | 0.012406 | 0.0011258 | 0.048493 | 0.013265 | 0.012406 | 0.0011258 | 0.048493 | 0.013265 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0.055849 | 0.01339 | 0.014074 | 0.0035312 | 0.014074 | 0.0035312 | 0.055849 | 0.01339 | 0.014074 | 0.0035312 | 0.055849 | 0.01339 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 8.7379e-05 | 0.0005527 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 8.7471e-05 | 0.00054755 | 2.8701e-05 | 0.00021878 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 0.0062563 | 0.039573 | 0.002055 | 0.015665 | 0.0020519 | 0.012615 | 0.0062629 | 0.039204 | 0.002055 | 0.015665 | 0.0062563 | 0.039573 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055229 | 0.034934 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020473 | 0.01295 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0084702 | 0.053577 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0080986 | 0.051226 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0071887 | 0.045471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072059 | 0.045579 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014563 | 0.00092117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012924 | 0.00053241 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03114 | 0.012828 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040892 | 0.016846 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036855 | 0.0015183 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034356 | 0.014153 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066083 | 0.027224 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049012 | 0.020191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027042 | 0.01114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 0.0079847 | 0.049224 | 0.0028505 | 0.020002 | 0.0028442 | 0.016264 | 0.0054276 | 0.046701 | 0.0028505 | 0.020002 | 0.0079847 | 0.049224 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 0.0020197 | 0.00083202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 0.053479 | 0.022031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 0.096145 | 0.039608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 0.0035317 | 0.021772 | 0.0012608 | 0.0088473 | 0.001258 | 0.0071937 | 0.0024007 | 0.020656 | 0.0012608 | 0.0088473 | 0.0035317 | 0.021772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 0.0044001 | 0.038301 | 0.0023163 | 0.016254 | 0.0023112 | 0.013216 | 0.006499 | 0.03965 | 0.0023163 | 0.016254 | 0.0064885 | 0.040001 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0024425 | 0.01545 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 0.0034016 | 0.02097 | 0.0012143 | 0.0085213 | 0.0012117 | 0.0069287 | 0.0023123 | 0.019895 | 0.0012143 | 0.0085213 | 0.0034016 | 0.02097 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 0.0036205 | 0.02232 | 0.0012925 | 0.0090697 | 0.0012896 | 0.0073746 | 0.0024611 | 0.021176 | 0.0012925 | 0.0090697 | 0.0036205 | 0.02232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 0.0047859 | 0.029504 | 0.0017085 | 0.011989 | 0.0017047 | 0.0097483 | 0.0032532 | 0.027992 | 0.0017085 | 0.011989 | 0.0047859 | 0.029504 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052678 | 0.0021701 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061216 | 0.025219 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07911 | 0.03259 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074872 | 0.030844 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052506 | 0.002163 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10989 | 0.045269 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025995 | 0.010709 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064887 | 0.026731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061005 | 0.025132 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056123 | 0.02312 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 0.0032249 | 0.019881 | 0.0011513 | 0.0080788 | 0.0011487 | 0.0065689 | 0.0021922 | 0.018862 | 0.0011513 | 0.0080788 | 0.0032249 | 0.019881 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 0.0034551 | 0.0213 | 0.0012334 | 0.0086553 | 0.0012307 | 0.0070377 | 0.0023486 | 0.020208 | 0.0012334 | 0.0086553 | 0.0034551 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 0.0035001 | 0.021578 | 0.0012495 | 0.0087681 | 0.0012467 | 0.0071293 | 0.0023792 | 0.020471 | 0.0012495 | 0.0087681 | 0.0035001 | 0.021578 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0.0035259 | 0.021737 | 0.0012587 | 0.0088328 | 0.001256 | 0.007182 | 0.0023968 | 0.020623 | 0.0012587 | 0.0088328 | 0.0035259 | 0.021737 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 0.0012678 | 0.00052229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 0.074899 | 0.030856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 0.037656 | 0.015513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 0.028307 | 0.011661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 0.018688 | 0.0076987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 0.066818 | 0.027526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013022 | 0.00053646 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023049 | 0.0094953 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089334 | 0.036802 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061781 | 0.025451 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 0.004145 | 0.025553 | 0.0014797 | 0.010384 | 0.0014764 | 0.0084428 | 0.0028176 | 0.024243 | 0.0014797 | 0.010384 | 0.004145 | 0.025553 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 0.0050049 | 0.0020618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 0.063074 | 0.025984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 0.0036506 | 0.022505 | 0.0013032 | 0.0091451 | 0.0013004 | 0.0074359 | 0.0024815 | 0.021352 | 0.0013032 | 0.0091451 | 0.0036506 | 0.022505 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 0.0035186 | 0.021692 | 0.0012561 | 0.0088145 | 0.0012534 | 0.0071671 | 0.0023918 | 0.02058 | 0.0012561 | 0.0088145 | 0.0035186 | 0.021692 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 0.0033321 | 0.00091151 | 0.00085243 | 7.7361e-05 | 0.00085243 | 7.7361e-05 | 0.0033321 | 0.00091151 | 0.00085243 | 7.7361e-05 | 0.0033321 | 0.00091151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 0.028431 | 0.0077774 | 0.0072733 | 0.00066008 | 0.0072733 | 0.00066008 | 0.028431 | 0.0077774 | 0.0072733 | 0.00066008 | 0.028431 | 0.0077774 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 0.0040699 | 0.023281 | 0.0011406 | 0.0086943 | 0.0011389 | 0.0070015 | 0.0018673 | 0.019831 | 0.0011406 | 0.0086943 | 0.0040699 | 0.023281 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 0.0038576 | 0.022066 | 0.0010811 | 0.0082407 | 0.0010794 | 0.0066362 | 0.0017699 | 0.018796 | 0.0010811 | 0.0082407 | 0.0038576 | 0.022066 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 0.0038794 | 0.022191 | 0.0010872 | 0.0082874 | 0.0010855 | 0.0066738 | 0.0017799 | 0.018903 | 0.0010872 | 0.0082874 | 0.0038794 | 0.022191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 0.0042775 | 0.024468 | 0.0011988 | 0.0091377 | 0.0011969 | 0.0073586 | 0.0019625 | 0.020842 | 0.0011988 | 0.0091377 | 0.0042775 | 0.024468 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 0.017184 | 0.010433 | 0.012836 | 0.0024936 | 0.012836 | 0.0024936 | 0.017184 | 0.010433 | 0.012836 | 0.0024936 | 0.017184 | 0.010433 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 0.0034005 | 0.019451 | 0.00095298 | 0.0072642 | 0.00095153 | 0.0058498 | 0.0015602 | 0.016569 | 0.00095298 | 0.0072642 | 0.0034005 | 0.019451 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0.090044 | 0.037095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 0.04954 | 0.020409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 0.0040088 | 0.022931 | 0.0011235 | 0.0085637 | 0.0011218 | 0.0068964 | 0.0018393 | 0.019533 | 0.0011235 | 0.0085637 | 0.0040088 | 0.022931 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 0.0038009 | 0.021742 | 0.0010652 | 0.0081196 | 0.0010636 | 0.0065387 | 0.0017439 | 0.01852 | 0.0010652 | 0.0081196 | 0.0038009 | 0.021742 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 0.00010241 | 0.00058582 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 4.6988e-05 | 0.00049902 | 2.8701e-05 | 0.00021878 | 0.00010241 | 0.00058582 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0.0010541 | 0.015854 | 0.00063209 | 0.006817 | 0.00063348 | 0.0054459 | 0.0010514 | 0.015682 | 0.00063209 | 0.006817 | 0.0010541 | 0.015854 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 0.0014203 | 0.021362 | 0.00085169 | 0.0091854 | 0.00085357 | 0.007338 | 0.0014167 | 0.02113 | 0.00085169 | 0.0091854 | 0.0014203 | 0.021362 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 0.00064333 | 0.009676 | 0.00038577 | 0.0041605 | 0.00038662 | 0.0033237 | 0.00064169 | 0.009571 | 0.00038577 | 0.0041605 | 0.00064333 | 0.009676 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 0.0010782 | 0.016216 | 0.00064652 | 0.0069727 | 0.00064795 | 0.0055703 | 0.0010754 | 0.01604 | 0.00064652 | 0.0069727 | 0.0010782 | 0.016216 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 7.015e-05 | 0.0010551 | 4.2065e-05 | 0.00045367 | 4.2158e-05 | 0.00036242 | 6.9971e-05 | 0.0010436 | 4.2065e-05 | 0.00045367 | 7.015e-05 | 0.0010551 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 0.0015598 | 0.023459 | 0.00093529 | 0.010087 | 0.00093736 | 0.0080583 | 0.0015558 | 0.023205 | 0.00093529 | 0.010087 | 0.0015598 | 0.023459 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 0.0011637 | 0.017502 | 0.0006978 | 0.0075257 | 0.00069934 | 0.0060121 | 0.0011607 | 0.017312 | 0.0006978 | 0.0075257 | 0.0011637 | 0.017502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 0.0013849 | 0.02083 | 0.00083046 | 0.0089564 | 0.00083229 | 0.0071551 | 0.0013814 | 0.020604 | 0.00083046 | 0.0089564 | 0.0013849 | 0.02083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 6.5675e-05 | 0.00053684 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 6.5766e-05 | 0.00053169 | 2.8701e-05 | 0.00021878 | 6.5675e-05 | 0.00053684 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 0.010999 | 0.0066774 | 0.0082156 | 0.001596 | 0.0082156 | 0.001596 | 0.010999 | 0.0066774 | 0.0082156 | 0.001596 | 0.010999 | 0.0066774 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 0.024205 | 0.014696 | 0.018081 | 0.0035124 | 0.018081 | 0.0035124 | 0.024205 | 0.014696 | 0.018081 | 0.0035124 | 0.024205 | 0.014696 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 0.029391 | 0.017844 | 0.021955 | 0.0042649 | 0.021955 | 0.0042649 | 0.029391 | 0.017844 | 0.021955 | 0.0042649 | 0.029391 | 0.017844 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 0.039457 | 0.023955 | 0.029473 | 0.0057255 | 0.029473 | 0.0057255 | 0.039457 | 0.023955 | 0.029473 | 0.0057255 | 0.039457 | 0.023955 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 0.034549 | 0.020975 | 0.025807 | 0.0050133 | 0.025807 | 0.0050133 | 0.034549 | 0.020975 | 0.025807 | 0.0050133 | 0.034549 | 0.020975 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 0.034679 | 0.021054 | 0.025905 | 0.0050323 | 0.025905 | 0.0050323 | 0.034679 | 0.021054 | 0.025905 | 0.0050323 | 0.034679 | 0.021054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 0.043774 | 0.026576 | 0.032698 | 0.006352 | 0.032698 | 0.006352 | 0.043774 | 0.026576 | 0.032698 | 0.006352 | 0.043774 | 0.026576 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 0.030863 | 0.018737 | 0.023054 | 0.0044785 | 0.023054 | 0.0044785 | 0.030863 | 0.018737 | 0.023054 | 0.0044785 | 0.030863 | 0.018737 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 0.010882 | 0.0066069 | 0.0081289 | 0.0015791 | 0.0081289 | 0.0015791 | 0.010882 | 0.0066069 | 0.0081289 | 0.0015791 | 0.010882 | 0.0066069 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0.019494 | 0.011835 | 0.014561 | 0.0028287 | 0.014561 | 0.0028287 | 0.019494 | 0.011835 | 0.014561 | 0.0028287 | 0.019494 | 0.011835 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0.039917 | 0.024234 | 0.029817 | 0.0057923 | 0.029817 | 0.0057923 | 0.039917 | 0.024234 | 0.029817 | 0.0057923 | 0.039917 | 0.024234 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0.020241 | 0.012288 | 0.015119 | 0.0029371 | 0.015119 | 0.0029371 | 0.020241 | 0.012288 | 0.015119 | 0.0029371 | 0.020241 | 0.012288 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0.005408 | 0.0032833 | 0.0040396 | 0.00078474 | 0.0040396 | 0.00078474 | 0.005408 | 0.0032833 | 0.0040396 | 0.00078474 | 0.005408 | 0.0032833 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0.00072194 | 0.0004383 | 0.00053927 | 0.00010476 | 0.00053927 | 0.00010476 | 0.00072194 | 0.0004383 | 0.00053927 | 0.00010476 | 0.00072194 | 0.0004383 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 4.6582e-05 | 0.00050177 | 2.8387e-05 | 0.00021636 | 2.8344e-05 | 0.00017379 | 4.6674e-05 | 0.00049657 | 2.8387e-05 | 0.00021636 | 4.6582e-05 | 0.00050177 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 0.0015641 | 0.016848 | 0.00095315 | 0.0072645 | 0.00095168 | 0.0058351 | 0.0015671 | 0.016673 | 0.00095315 | 0.0072645 | 0.0015641 | 0.016848 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 0.062263 | 0.014927 | 0.015691 | 0.0039368 | 0.015691 | 0.0039368 | 0.062263 | 0.014927 | 0.015691 | 0.0039368 | 0.062263 | 0.014927 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018586 | 0.010402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 0.10203 | 0.024461 | 0.025712 | 0.006451 | 0.025712 | 0.006451 | 0.10203 | 0.024461 | 0.025712 | 0.006451 | 0.10203 | 0.024461 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 0.024065 | 0.014611 | 0.017976 | 0.0034921 | 0.017976 | 0.0034921 | 0.024065 | 0.014611 | 0.017976 | 0.0034921 | 0.024065 | 0.014611 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 0.0019897 | 0.021432 | 0.0012125 | 0.0092413 | 0.0012106 | 0.007423 | 0.0019936 | 0.02121 | 0.0012125 | 0.0092413 | 0.0019897 | 0.021432 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 2.9968e-05 | 0.00032281 | 1.8262e-05 | 0.00013919 | 1.8234e-05 | 0.0001118 | 3.0027e-05 | 0.00031946 | 1.8262e-05 | 0.00013919 | 2.9968e-05 | 0.00032281 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 5.0211e-05 | 0.00021125 | 3.1545e-05 | 0.00010297 | 3.1336e-05 | 8.8957e-05 | 5.0631e-05 | 0.00021036 | 3.1545e-05 | 0.00010297 | 5.0211e-05 | 0.00021125 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 0.00026518 | 0.0011156 | 0.0001666 | 0.0005438 | 0.00016549 | 0.0004698 | 0.00026739 | 0.001111 | 0.0001666 | 0.0005438 | 0.00026518 | 0.0011156 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0.00025419 | 0.0010694 | 0.00015969 | 0.00052128 | 0.00015864 | 0.00045035 | 0.00025632 | 0.001065 | 0.00015969 | 0.00052128 | 0.00025419 | 0.0010694 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 4.2888e-05 | 0.00018044 | 2.6944e-05 | 8.7953e-05 | 2.6766e-05 | 7.5984e-05 | 4.3247e-05 | 0.00017968 | 2.6944e-05 | 8.7953e-05 | 4.2888e-05 | 0.00018044 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 3.1415e-05 | 0.00035448 | 1.8925e-05 | 0.00014424 | 1.8896e-05 | 0.00011586 | 3.1476e-05 | 0.00035101 | 1.8925e-05 | 0.00014424 | 3.1415e-05 | 0.00035448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 0.0018538 | 0.020918 | 0.0011168 | 0.0085115 | 0.001115 | 0.0068367 | 0.0018574 | 0.020713 | 0.0011168 | 0.0085115 | 0.0018538 | 0.020918 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 0.0023446 | 0.026457 | 0.0014125 | 0.010765 | 0.0014103 | 0.008647 | 0.0023492 | 0.026198 | 0.0014125 | 0.010765 | 0.0023446 | 0.026457 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 0.0019837 | 0.022384 | 0.001195 | 0.0091079 | 0.0011932 | 0.0073158 | 0.0019875 | 0.022165 | 0.001195 | 0.0091079 | 0.0019837 | 0.022384 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0.00039589 | 9.4914e-05 | 9.9766e-05 | 2.5031e-05 | 9.9766e-05 | 2.5031e-05 | 0.00039589 | 9.4914e-05 | 9.9766e-05 | 2.5031e-05 | 0.00039589 | 9.4914e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 0.034844 | 0.0083538 | 0.0087809 | 0.0022031 | 0.0087809 | 0.0022031 | 0.034844 | 0.0083538 | 0.0087809 | 0.0022031 | 0.034844 | 0.0083538 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 0.0022612 | 0.025516 | 0.0013622 | 0.010382 | 0.0013601 | 0.0083394 | 0.0022656 | 0.025266 | 0.0013622 | 0.010382 | 0.0022612 | 0.025516 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019861 | 0.00062828 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.143e-05 | 0.00025759 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054817 | 0.01734 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0070851 | 0.022413 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098822 | 0.031261 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004422 | 0.02797 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043387 | 0.027443 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 0.010551 | 0.0064059 | 0.0078815 | 0.0015311 | 0.0078815 | 0.0015311 | 0.010551 | 0.0064059 | 0.0078815 | 0.0015311 | 0.010551 | 0.0064059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0.0023644 | 0.02668 | 0.0014244 | 0.010856 | 0.0014222 | 0.00872 | 0.002369 | 0.026419 | 0.0014244 | 0.010856 | 0.0023644 | 0.02668 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 0.0022488 | 0.025376 | 0.0013547 | 0.010325 | 0.0013526 | 0.0082936 | 0.0022532 | 0.025127 | 0.0013547 | 0.010325 | 0.0022488 | 0.025376 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 0.032991 | 0.01031 | 0.0084198 | 0.00085323 | 0.0084198 | 0.00085323 | 0.032991 | 0.01031 | 0.0084198 | 0.00085323 | 0.032991 | 0.01031 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 0.0019634 | 0.022155 | 0.0011828 | 0.0090148 | 0.001181 | 0.0072411 | 0.0019672 | 0.021938 | 0.0011828 | 0.0090148 | 0.0019634 | 0.022155 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 0.0054136 | 0.023552 | 0.0015707 | 0.0091379 | 0.0015649 | 0.0073814 | 0.0054254 | 0.023344 | 0.0015707 | 0.0091379 | 0.0054136 | 0.023552 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 0.0049997 | 0.021751 | 0.0014505 | 0.0084392 | 0.0014452 | 0.0068169 | 0.0050105 | 0.021559 | 0.0014505 | 0.0084392 | 0.0049997 | 0.021751 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 0.0017138 | 0.019339 | 0.0010324 | 0.0078689 | 0.0010309 | 0.0063206 | 0.0017171 | 0.01915 | 0.0010324 | 0.0078689 | 0.0017138 | 0.019339 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 8.7379e-05 | 0.0005527 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 8.7471e-05 | 0.00054755 | 2.8701e-05 | 0.00021878 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2.4757e-05 | 0.0001566 | 8.1321e-06 | 6.1987e-05 | 8.1197e-06 | 4.9918e-05 | 2.4783e-05 | 0.00015514 | 8.1321e-06 | 6.1987e-05 | 2.4757e-05 | 0.0001566 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 0.0021487 | 0.013591 | 0.00070577 | 0.0053798 | 0.00070469 | 0.0043323 | 0.0021509 | 0.013464 | 0.00070577 | 0.0053798 | 0.0021487 | 0.013591 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0.0027795 | 0.017581 | 0.00091299 | 0.0069594 | 0.0009116 | 0.0056044 | 0.0027824 | 0.017418 | 0.00091299 | 0.0069594 | 0.0027795 | 0.017581 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 0.0027854 | 0.017618 | 0.0009149 | 0.0069739 | 0.00091351 | 0.0056161 | 0.0027883 | 0.017454 | 0.0009149 | 0.0069739 | 0.0027854 | 0.017618 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 0.0028468 | 0.018007 | 0.00093509 | 0.0071278 | 0.00093366 | 0.00574 | 0.0028498 | 0.017839 | 0.00093509 | 0.0071278 | 0.0028468 | 0.018007 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 0.00013993 | 3.8277e-05 | 3.5796e-05 | 3.2486e-06 | 3.5796e-05 | 3.2486e-06 | 0.00013993 | 3.8277e-05 | 3.5796e-05 | 3.2486e-06 | 0.00013993 | 3.8277e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 0.010571 | 0.0028917 | 0.0027043 | 0.00024542 | 0.0027043 | 0.00024542 | 0.010571 | 0.0028917 | 0.0027043 | 0.00024542 | 0.010571 | 0.0028917 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 0.0019356 | 0.021841 | 0.0011661 | 0.0088872 | 0.0011643 | 0.0071385 | 0.0019394 | 0.021628 | 0.0011661 | 0.0088872 | 0.0019356 | 0.021841 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 0.00092166 | 0.00025212 | 0.00023578 | 2.1398e-05 | 0.00023578 | 2.1398e-05 | 0.00092166 | 0.00025212 | 0.00023578 | 2.1398e-05 | 0.00092166 | 0.00025212 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 0.028379 | 0.0077631 | 0.00726 | 0.00065886 | 0.00726 | 0.00065886 | 0.028379 | 0.0077631 | 0.00726 | 0.00065886 | 0.028379 | 0.0077631 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 0.0019439 | 0.021935 | 0.0011711 | 0.0089254 | 0.0011693 | 0.0071692 | 0.0019477 | 0.021721 | 0.0011711 | 0.0089254 | 0.0019439 | 0.021935 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 0.0019659 | 0.022184 | 0.0011843 | 0.0090264 | 0.0011825 | 0.0072503 | 0.0019697 | 0.021966 | 0.0011843 | 0.0090264 | 0.0019659 | 0.022184 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 0.028673 | 0.0089608 | 0.0073176 | 0.00074154 | 0.0073176 | 0.00074154 | 0.028673 | 0.0089608 | 0.0073176 | 0.00074154 | 0.028673 | 0.0089608 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0.0085309 | 0.037114 | 0.0024751 | 0.0144 | 0.002466 | 0.011632 | 0.0085495 | 0.036786 | 0.0024751 | 0.0144 | 0.0085309 | 0.037114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 0.0089497 | 0.038936 | 0.0025966 | 0.015107 | 0.002587 | 0.012203 | 0.0089692 | 0.038591 | 0.0025966 | 0.015107 | 0.0089497 | 0.038936 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0071571 | 0.044802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 0.001795 | 0.020255 | 0.0010814 | 0.0082417 | 0.0010797 | 0.0066201 | 0.0017985 | 0.020057 | 0.0010814 | 0.0082417 | 0.001795 | 0.020255 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 0.0015926 | 0.017971 | 0.00095939 | 0.0073121 | 0.00095792 | 0.0058734 | 0.0015957 | 0.017795 | 0.00095939 | 0.0073121 | 0.0015926 | 0.017971 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 0.071488 | 0.017139 | 0.018015 | 0.00452 | 0.018015 | 0.00452 | 0.071488 | 0.017139 | 0.018015 | 0.00452 | 0.071488 | 0.017139 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 0.063232 | 0.017297 | 0.016176 | 0.001468 | 0.016176 | 0.001468 | 0.063232 | 0.017297 | 0.016176 | 0.001468 | 0.063232 | 0.017297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 0.0089643 | 0.0054424 | 0.0066961 | 0.0013008 | 0.0066961 | 0.0013008 | 0.0089643 | 0.0054424 | 0.0066961 | 0.0013008 | 0.0089643 | 0.0054424 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 0.0023907 | 0.026976 | 0.0014402 | 0.010976 | 0.001438 | 0.0088167 | 0.0023953 | 0.026712 | 0.0014402 | 0.010976 | 0.0023907 | 0.026976 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 4.7122e-05 | 0.00053173 | 2.8387e-05 | 0.00021636 | 2.8344e-05 | 0.00017379 | 4.7213e-05 | 0.00052652 | 2.8387e-05 | 0.00021636 | 4.7122e-05 | 0.00053173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 3.33e-05 | 0.00037575 | 2.006e-05 | 0.00015289 | 2.0029e-05 | 0.00012281 | 3.3364e-05 | 0.00037208 | 2.006e-05 | 0.00015289 | 3.33e-05 | 0.00037575 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 0.0018938 | 0.02137 | 0.0011409 | 0.0086954 | 0.0011391 | 0.0069845 | 0.0018975 | 0.021161 | 0.0011409 | 0.0086954 | 0.0018938 | 0.02137 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 0.00072846 | 0.00022766 | 0.00018591 | 1.884e-05 | 0.00018591 | 1.884e-05 | 0.00072846 | 0.00022766 | 0.00018591 | 1.884e-05 | 0.00072846 | 0.00022766 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 0.030478 | 0.009525 | 0.0077784 | 0.00078823 | 0.0077784 | 0.00078823 | 0.030478 | 0.009525 | 0.0077784 | 0.00078823 | 0.030478 | 0.009525 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 0.0020131 | 0.022715 | 0.0012127 | 0.0092427 | 0.0012108 | 0.0074241 | 0.002017 | 0.022493 | 0.0012127 | 0.0092427 | 0.0020131 | 0.022715 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 0.0028738 | 0.032428 | 0.0017312 | 0.013195 | 0.0017286 | 0.010599 | 0.0028794 | 0.032111 | 0.0017312 | 0.013195 | 0.0028738 | 0.032428 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 0.0016994 | 0.018269 | 0.00104 | 0.0079278 | 0.0010385 | 0.0063843 | 0.0017027 | 0.018083 | 0.00104 | 0.0079278 | 0.0016994 | 0.018269 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | 0.005273 | 0.033354 | 0.001732 | 0.013203 | 0.0017294 | 0.010632 | 0.0052786 | 0.033043 | 0.001732 | 0.013203 | 0.005273 | 0.033354 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 0.00014126 | 0.00089353 | 4.6401e-05 | 0.00035369 | 4.633e-05 | 0.00028483 | 0.00014141 | 0.0008852 | 4.6401e-05 | 0.00035369 | 0.00014126 | 0.00089353 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030137 | 0.019063 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049943 | 0.03159 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 0.0019582 | 0.029452 | 0.0011742 | 0.012664 | 0.0011768 | 0.010117 | 0.0019532 | 0.029133 | 0.0011742 | 0.012664 | 0.0019582 | 0.029452 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 0.0016264 | 0.024462 | 0.00097527 | 0.010518 | 0.00097743 | 0.0084027 | 0.0016223 | 0.024196 | 0.00097527 | 0.010518 | 0.0016264 | 0.024462 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 0.00032837 | 0.0026842 | 0.00014351 | 0.0010939 | 0.00014329 | 0.00088091 | 0.00032883 | 0.0026585 | 0.00014351 | 0.0010939 | 0.00032837 | 0.0026842 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 0.00061196 | 0.0092042 | 0.00036696 | 0.0039576 | 0.00036777 | 0.0031616 | 0.0006104 | 0.0091043 | 0.00036696 | 0.0039576 | 0.00061196 | 0.0092042 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 0.00067129 | 0.0031187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 0.0080002 | 0.037168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | 0.0068324 | 0.031743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | 0.0064389 | 0.029915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 0.0064929 | 0.030165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 0.0063207 | 0.029365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 0.0056904 | 0.035994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | 0.0062377 | 0.039455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | 0.0019317 | 0.029054 | 0.0011584 | 0.012493 | 0.0011609 | 0.0099802 | 0.0019268 | 0.028739 | 0.0011584 | 0.012493 | 0.0019317 | 0.029054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 0.0014991 | 0.022547 | 0.00089891 | 0.0096947 | 0.0009009 | 0.0077448 | 0.0014952 | 0.022302 | 0.00089891 | 0.0096947 | 0.0014991 | 0.022547 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 0.0012787 | 0.019232 | 0.00076677 | 0.0082696 | 0.00076847 | 0.0066064 | 0.0012754 | 0.019024 | 0.00076677 | 0.0082696 | 0.0012787 | 0.019232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7471e-05 | 0.00054755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00017407 | 0.0010896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037583 | 0.023526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043254 | 0.027076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034945 | 0.021875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005101 | 0.031931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007414 | 0.04641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056623 | 0.035445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019775 | 0.00058189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093556 | 0.027529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0061079 | 0.017973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098196 | 0.028895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009697 | 0.028534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010302 | 0.030315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013107 | 0.038568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012158 | 0.035775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010555 | 0.031058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010003 | 0.029434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0091453 | 0.026911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098446 | 0.042358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013171 | 0.00056669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026078 | 0.001122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064966 | 0.027953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0063825 | 0.027462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0042677 | 0.026715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043295 | 0.027102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00065633 | 0.002824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049877 | 0.02146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065129 | 0.028023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053846 | 0.023168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073444 | 0.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064092 | 0.027577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065225 | 0.028064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062165 | 0.026748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 0.0014429 | 0.021701 | 0.00086521 | 0.0093312 | 0.00086712 | 0.0074545 | 0.0014392 | 0.021466 | 0.00086521 | 0.0093312 | 0.0014429 | 0.021701 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 0.00032837 | 0.0026842 | 0.00014351 | 0.0010939 | 0.00014329 | 0.00088091 | 0.00032883 | 0.0026585 | 0.00014351 | 0.0010939 | 0.00032837 | 0.0026842 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 0.0015636 | 0.023517 | 0.00093758 | 0.010112 | 0.00093965 | 0.008078 | 0.0015596 | 0.023261 | 0.00093758 | 0.010112 | 0.0015636 | 0.023517 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 0.0033924 | 0.031704 | 0.0011733 | 0.012654 | 0.0011759 | 0.010109 | 0.0033874 | 0.031385 | 0.0011733 | 0.012654 | 0.0033924 | 0.031704 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 0.0010013 | 0.01506 | 0.00060041 | 0.0064753 | 0.00060173 | 0.005173 | 0.00099871 | 0.014896 | 0.00060041 | 0.0064753 | 0.0010013 | 0.01506 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 0.0015778 | 0.023731 | 0.00094614 | 0.010204 | 0.00094823 | 0.0081517 | 0.0015738 | 0.023474 | 0.00094614 | 0.010204 | 0.0015778 | 0.023731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014469 | 0.00058252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00055417 | 0.002231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078341 | 0.031539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066949 | 0.026953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00676 | 0.027215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 0.0014705 | 0.022118 | 0.0008818 | 0.0095101 | 0.00088375 | 0.0075974 | 0.0014668 | 0.021877 | 0.0008818 | 0.0095101 | 0.0014705 | 0.022118 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 0.0014343 | 0.021572 | 0.00086005 | 0.0092755 | 0.00086195 | 0.00741 | 0.0014306 | 0.021338 | 0.00086005 | 0.0092755 | 0.0014343 | 0.021572 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 0.001685 | 0.025343 | 0.0010104 | 0.010897 | 0.0010126 | 0.0087055 | 0.0016807 | 0.025068 | 0.0010104 | 0.010897 | 0.001685 | 0.025343 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 0.00013142 | 0.00057175 | 3.8129e-05 | 0.00022183 | 3.7989e-05 | 0.00017919 | 0.00013171 | 0.00056669 | 3.8129e-05 | 0.00022183 | 0.00013142 | 0.00057175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 0.00037586 | 0.0016352 | 0.00010905 | 0.00063444 | 0.00010865 | 0.00051248 | 0.00037668 | 0.0016207 | 0.00010905 | 0.00063444 | 0.00037586 | 0.0016352 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 0.0064015 | 0.02785 | 0.0018573 | 0.010805 | 0.0018504 | 0.0087283 | 0.0064154 | 0.027603 | 0.0018573 | 0.010805 | 0.0064015 | 0.02785 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 0.0016868 | 0.02537 | 0.0010115 | 0.010908 | 0.0010137 | 0.0087145 | 0.0016825 | 0.025094 | 0.0010115 | 0.010908 | 0.0016868 | 0.02537 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 0.0010923 | 0.016429 | 0.00065501 | 0.0070643 | 0.00065646 | 0.0056435 | 0.0010895 | 0.016251 | 0.00065501 | 0.0070643 | 0.0010923 | 0.016429 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2.1892e-05 | 0.00017895 | 9.5671e-06 | 7.2926e-05 | 9.5525e-06 | 5.8727e-05 | 2.1922e-05 | 0.00017723 | 9.5671e-06 | 7.2926e-05 | 2.1892e-05 | 0.00017895 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 0.00010946 | 0.00089474 | 4.7836e-05 | 0.00036463 | 4.7763e-05 | 0.00029364 | 0.00010961 | 0.00088615 | 4.7836e-05 | 0.00036463 | 0.00010946 | 0.00089474 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 0.0016091 | 0.019251 | 0.0011076 | 0.0084427 | 0.0011059 | 0.0067989 | 0.0016126 | 0.019052 | 0.0011076 | 0.0084427 | 0.0016091 | 0.019251 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 5.7165e-05 | 0.00036157 | 1.8925e-05 | 0.00014424 | 1.8896e-05 | 0.00011586 | 5.7226e-05 | 0.0003581 | 1.8925e-05 | 0.00014424 | 5.7165e-05 | 0.00036157 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 0.0025916 | 0.031005 | 0.0017839 | 0.013598 | 0.0017812 | 0.01095 | 0.0025973 | 0.030685 | 0.0017839 | 0.013598 | 0.0025916 | 0.031005 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 0.0019921 | 0.016284 | 0.00087061 | 0.0066363 | 0.00086928 | 0.0053442 | 0.0019949 | 0.016128 | 0.00087061 | 0.0066363 | 0.0019921 | 0.016284 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 0.004946 | 0.031285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019913 | 0.00062359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012744 | 0.003991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072669 | 0.022757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01087 | 0.034042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099744 | 0.031236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095051 | 0.029766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099419 | 0.031134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 0.0026791 | 0.0219 | 0.0011708 | 0.0089247 | 0.001169 | 0.0071871 | 0.0026828 | 0.02169 | 0.0011708 | 0.0089247 | 0.0026791 | 0.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 0.002984 | 0.024392 | 0.0013041 | 0.0099406 | 0.0013021 | 0.0080051 | 0.0029882 | 0.024158 | 0.0013041 | 0.0099406 | 0.002984 | 0.024392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 0.00387 | 0.031634 | 0.0016913 | 0.012892 | 0.0016887 | 0.010382 | 0.0038754 | 0.031331 | 0.0016913 | 0.012892 | 0.00387 | 0.031634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 0.0028258 | 0.023099 | 0.0012349 | 0.0094133 | 0.001233 | 0.0075805 | 0.0028297 | 0.022877 | 0.0012349 | 0.0094133 | 0.0028258 | 0.023099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 0.00013142 | 0.00057175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 0.004782 | 0.020804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 0.01081 | 0.047028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 0.0046448 | 0.0020179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 0.10246 | 0.044514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00052836 | 0.0016546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011948 | 0.0037415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052803 | 0.016535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011143 | 0.034894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012173 | 0.03812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010609 | 0.033223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 0.0041983 | 0.026555 | 0.001379 | 0.010512 | 0.0013769 | 0.008465 | 0.0042027 | 0.026308 | 0.001379 | 0.010512 | 0.0041983 | 0.026555 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 0.0038563 | 0.024392 | 0.0012667 | 0.0096555 | 0.0012648 | 0.0077755 | 0.0038604 | 0.024165 | 0.0012667 | 0.0096555 | 0.0038563 | 0.024392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 0.0040762 | 0.025783 | 0.0013389 | 0.010206 | 0.0013369 | 0.0082189 | 0.0040805 | 0.025543 | 0.0013389 | 0.010206 | 0.0040762 | 0.025783 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 0.0040069 | 0.025345 | 0.0013162 | 0.010032 | 0.0013141 | 0.0080791 | 0.0040111 | 0.025109 | 0.0013162 | 0.010032 | 0.0040069 | 0.025345 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 0.0041374 | 0.02617 | 0.001359 | 0.010359 | 0.0013569 | 0.0083422 | 0.0041417 | 0.025926 | 0.001359 | 0.010359 | 0.0041374 | 0.02617 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 0.0041651 | 0.026345 | 0.0013681 | 0.010428 | 0.001366 | 0.008398 | 0.0041694 | 0.0261 | 0.0013681 | 0.010428 | 0.0041651 | 0.026345 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 0.0044788 | 0.02833 | 0.0014711 | 0.011214 | 0.0014689 | 0.0090305 | 0.0044835 | 0.028066 | 0.0014711 | 0.011214 | 0.0044788 | 0.02833 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 0.00054845 | 0.0034691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 0.0047622 | 0.030122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 0.0049856 | 0.031535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 0.004445 | 0.028116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 0.0047849 | 0.030266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 0.0097928 | 0.042802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 0.0082247 | 0.035948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 0.0048744 | 0.021305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 0.0060145 | 0.026288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 0.0054518 | 0.023718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 0.0083264 | 0.036224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 0.0063531 | 0.029595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 0.0047135 | 0.029814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019913 | 0.00062359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012147 | 0.0038039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0075125 | 0.023526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
377 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008844 | 0.027696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055031 | 0.034448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047645 | 0.029825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049421 | 0.030936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044216 | 0.027679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010002 | 0.031323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099704 | 0.031223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010959 | 0.03432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097627 | 0.030572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
386 | 0.0033527 | 0.021207 | 0.0011013 | 0.0083946 | 0.0010996 | 0.0067601 | 0.0033563 | 0.021009 | 0.0011013 | 0.0083946 | 0.0033527 | 0.021207 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387 | 0.0046343 | 0.029313 | 0.0015222 | 0.011603 | 0.0015199 | 0.0093441 | 0.0046392 | 0.02904 | 0.0015222 | 0.011603 | 0.0046343 | 0.029313 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388 | 0.0048262 | 0.030527 | 0.0015853 | 0.012084 | 0.0015829 | 0.0097311 | 0.0048313 | 0.030243 | 0.0015853 | 0.012084 | 0.0048262 | 0.030527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
389 | 0.0045932 | 0.029054 | 0.0015087 | 0.0115 | 0.0015064 | 0.0092613 | 0.004598 | 0.028783 | 0.0015087 | 0.0115 | 0.0045932 | 0.029054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
390 | 0.0041823 | 0.026454 | 0.0013737 | 0.010471 | 0.0013716 | 0.0084327 | 0.0041866 | 0.026207 | 0.0013737 | 0.010471 | 0.0041823 | 0.026454 | 0 | 0 | 0 | 0 | 0 | 0 | 0
391 | 0.0056383 | 0.035664 | 0.001852 | 0.014117 | 0.0018492 | 0.011368 | 0.0056442 | 0.035331 | 0.001852 | 0.014117 | 0.0056383 | 0.035664 | 0 | 0 | 0 | 0 | 0 | 0 | 0
392 | 0.004662 | 0.029488 | 0.0015313 | 0.011673 | 0.001529 | 0.0093999 | 0.0046669 | 0.029214 | 0.0015313 | 0.011673 | 0.004662 | 0.029488 | 0 | 0 | 0 | 0 | 0 | 0 | 0
393 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00016033 | 0.00066615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
394 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026851 | 0.0016979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
395 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052603 | 0.018009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093107 | 0.031876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010297 | 0.035254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
398 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0089934 | 0.030789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044137 | 0.015111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
400 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088468 | 0.030288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
401 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040831 | 0.02556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
402 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041858 | 0.026202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
403 | 0.0041217 | 0.026071 | 0.0013538 | 0.01032 | 0.0013518 | 0.0083105 | 0.004126 | 0.025828 | 0.0013538 | 0.01032 | 0.0041217 | 0.026071 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404 | 0.0063254 | 0.04001 | 0.0020777 | 0.015837 | 0.0020745 | 0.012754 | 0.006332 | 0.039637 | 0.0020777 | 0.015837 | 0.0063254 | 0.04001 | 0 | 0 | 0 | 0 | 0 | 0 | 0
405 | 0.0043058 | 0.027235 | 0.0014143 | 0.010781 | 0.0014122 | 0.0086817 | 0.0043103 | 0.026981 | 0.0014143 | 0.010781 | 0.0043058 | 0.027235 | 0 | 0 | 0 | 0 | 0 | 0 | 0
406 | 0.0072245 | 0.045697 | 0.002373 | 0.018089 | 0.0023694 | 0.014567 | 0.0072321 | 0.045271 | 0.002373 | 0.018089 | 0.0072245 | 0.045697 | 0 | 0 | 0 | 0 | 0 | 0 | 0
407 | 0.0082486 | 0.052175 | 0.0027094 | 0.020653 | 0.0027053 | 0.016632 | 0.0082572 | 0.051689 | 0.0027094 | 0.020653 | 0.0082486 | 0.052175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
408 | 0.0083523 | 0.052831 | 0.0027435 | 0.020912 | 0.0027393 | 0.016841 | 0.008361 | 0.052338 | 0.0027435 | 0.020912 | 0.0083523 | 0.052831 | 0 | 0 | 0 | 0 | 0 | 0 | 0
409 | 0.0073148 | 0.046268 | 0.0024027 | 0.018315 | 0.002399 | 0.014749 | 0.0073225 | 0.045837 | 0.0024027 | 0.018315 | 0.0073148 | 0.046268 | 0 | 0 | 0 | 0 | 0 | 0 | 0
410 | 0.0083185 | 0.052617 | 0.0027324 | 0.020828 | 0.0027282 | 0.016773 | 0.0083272 | 0.052127 | 0.0027324 | 0.020828 | 0.0083185 | 0.052617 | 0 | 0 | 0 | 0 | 0 | 0 | 0
411 | 0.008426 | 0.053297 | 0.0027677 | 0.021097 | 0.0027635 | 0.016989 | 0.0084348 | 0.0528 | 0.0027677 | 0.021097 | 0.008426 | 0.053297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
412 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
413 | 0.075142 | 0.023483 | 0.019177 | 0.0019433 | 0.019177 | 0.0019433 | 0.075142 | 0.023483 | 0.019177 | 0.0019433 | 0.075142 | 0.023483 | 0 | 0 | 0 | 0 | 0 | 0 | 0
414 | 0.046269 | 0.012657 | 0.011837 | 0.0010742 | 0.011837 | 0.0010742 | 0.046269 | 0.012657 | 0.011837 | 0.0010742 | 0.046269 | 0.012657 | 0 | 0 | 0 | 0 | 0 | 0 | 0
415 | 0.0036309 | 0.022966 | 0.0011926 | 0.009091 | 0.0011908 | 0.007321 | 0.0036347 | 0.022752 | 0.0011926 | 0.009091 | 0.0036309 | 0.022966 | 0 | 0 | 0 | 0 | 0 | 0 | 0
416 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
417 | 0.062836 | 0.019637 | 0.016036 | 0.0016251 | 0.016036 | 0.0016251 | 0.062836 | 0.019637 | 0.016036 | 0.0016251 | 0.062836 | 0.019637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
418 | 0.047695 | 0.014905 | 0.012172 | 0.0012335 | 0.012172 | 0.0012335 | 0.047695 | 0.014905 | 0.012172 | 0.0012335 | 0.047695 | 0.014905 | 0 | 0 | 0 | 0 | 0 | 0 | 0
419 | 0.015927 | 0.0096694 | 0.011897 | 0.0023111 | 0.011897 | 0.0023111 | 0.015927 | 0.0096694 | 0.011897 | 0.0023111 | 0.015927 | 0.0096694 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013142 | 0.00057175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065509 | 0.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0
422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00021903 | 0.00095291 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500 | 0.0922 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501 | 0.493 | 0.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502 | 0.366 | 0.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
503 | 0.3811 | 0.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504 | 0.819 | 0.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505 | 0.1872 | 0.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506 | 0.7114 | 0.2351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507 | 1.03 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
508 | 1.044 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509 | 0.1966 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510 | 0.3744 | 0.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
511 | 1.468 | 1.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512 | 0.5416 | 0.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
513 | 0.591 | 0.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514 | 0.7463 | 0.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
515 | 1.289 | 1.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516 | 0.732 | 0.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517 | 0.164 | 0.1565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
518 | 1.5042 | 1.3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
519 | 0.4095 | 0.4784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
520 | 0.7089 | 0.9373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521 | 0.4512 | 0.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
522 | 0.898 | 0.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
523 | 0.896 | 0.7011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
524 | 0.203 | 0.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
525 | 0.2842 | 0.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526 | 1.059 | 0.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527 | 0.8042 | 0.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
528 | 0.5075 | 0.2585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
529 | 0.9744 | 0.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
530 | 0.3105 | 0.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
531 | 0.341 | 0.5302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Configuration
No | Config | Phasing | Cable | SpacingID | PhA_ cond | PhB_ cond | PhC_ cond | Neu_Cond | Type | n | Outside diameter (Dod) | No of strands(k) (cable only!) | Relative permittivity (Cable!) | 1_flag | 2_flag | 3_flag | Neu_Flag_1 | Neu_Flag_2 | Neu_Flag_3 | dis Cable and neutral
1 | 1 | BACN | 601 | 1 | 2 | 2 | 2 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
2 | 2 | C A B N | 602 | 2 | 6 | 6 | 6 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
3 | 3 | CBN | 603 | 3 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 0 | 1 | 1 | 1 | 0 | 0
4 | 4 | CAN | 604 | 4 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 1 | 0 | 1 | 1 | 0 | 0
5 | 5 | CN | 605 | 5 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 0 | 0 | 1 | 1 | 0 | 0
6 | 6 | ABCN UG | 606 | 6 | 4 | 4 | 4 | 15 | 1 | 6 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 1 | 1
7 | 7 | AN UG TS | 607 | - | 16 | - | - | 9 | 2 | 3 | 0.88 | 5 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0.08333
8 | 8 | ABCN UG | 721 | 6 | 1 | 1 | 1 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
9 | 9 | ABCN UG | 722 | 6 | 3 | 3 | 3 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
10 | 10 | ABCN UG | 723 | 6 | 7 | 7 | 7 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
11 | 11 | ABCN UG | 724 | 6 | 10 | 10 | 10 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
12 | 12 | BACN | 300 | 1 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
13 | 13 | BACN | 301 | 1 | 11 | 11 | 11 | 11 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
14 | 14 | AN OH | 302 | 8 | 12 | 12 | 12 | 12 | 0 | 3 | 1.29 | 13 |  | 1 | 0 | 0 | 1 | 0 | 0
15 | 15 | BN OH | 303 | 9 | 12 | 12 | 12 | 12 | 0 | 3 | 1.29 | 13 |  | 0 | 1 | 0 | 1 | 0 | 0
16 | 16 | BN OH | 304 | 9 | 11 | 11 | 11 | 11 | 0 | 3 | 1.29 | 13 |  | 0 | 1 | 0 | 1 | 0 | 0
17 | 17 | ABC N OHL | 708 | 10 | 5 | 5 | 5 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
18 | 18 | ABC N OHL | 708 | 11 | 5 | 5 | 5 | 6 | 0 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
Note on J1: Author: 0 - OH Lines 1 - Concentric Neutral Cable 2 - Tape Shielded Cable
Note on K1: Author: Primitive size of Matrix

## Conductortype
No | Conductor | Type | Res. (Ohms/mi) | Dia. (Inch) | GMR (Ft) | Rating (Amps)
1 | 1,000,000 CM | AA | 0.105 | 1.15 | 0.0368 | 698
2 | 556,500 CM | ACSR | 0.186 | 0.927 | 0.0311 | 730
3 | 500,000 CM | AA | 0.206 | 0.813 | 0.026 | 483
4 | 250,000 CM | AA | 0.41 | 0.567 | 0.0171 | 329
5 | 336,400 CM | ACSR | 0.306 | 0.721 | 0.0244 | 530
6 | #4/0 | ACSR | 0.592 | 0.563 | 0.00814 | 340
7 | #2/0 | AA | 0.769 | 0.414 | 0.0125 | 230
8 | #1/0 | ACSR | 1.12 | 0.398 | 0.00446 | 230
9 | #1/0 | CU | 0.607 | 0.368 | 0.01113 | 310
10 | #2 | AA | 1.54 | 0.292 | 0.00883 | 156
11 | #2 | ACSR | 1.69 | 0.316 | 0.00418 | 180
12 | #4 | ACSR | 2.55 | 0.257 | 0.00452 | 140
13 | #10 | CU | 5.903 | 0.102 | 0.00331 | 80
14 | #12 | CU | 9.375 | 0.081 | 0.00262 | 75
15 | #14 | CU | 14.872 | 0.064 | 0.00208 | 20
16 | #1/0 | AA | 0.97 | 0.368 | 0.0111 | 202
17 | #4 | ACSR | 2.57 | 0.25 | 0.00437 | 140

## Spacing
SI No | Spacing No | n | X-PhaseCond1 | Y-PhaseCond2 | X-PhaseCond2 | Y-PhaseCond2 | X-PhaseCond3 | Y-PhaseCond3 | X-Neutral1 | Y-Neutral1 | X-Neutral2 | Y-Neutral2 | X-Neutral3 | Y-Neutral3
1 | 1 | 4 | 2.5 | 28 | 0 | 28 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
2 | 2 | 4 | 2.5 | 28 | 7 | 28 | 0 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
3 | 3 | 4 | 9999 | 9999 | 7 | 28 | 0 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
4 | 4 | 4 | 0 | 28 | 9999 | 9999 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
5 | 5 | 4 | 9999 | 9999 | 9999 | 9999 | 0 | 29 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
6 | 6 | 6 | 0 | 0 | 0.5 | 0 | 1 | 0 | 0 | 0.0511 | 0.5 | 0.0511 | 1 | 0.0511 | 515
7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 9999 | 9999 | 9999 | 9999
8 | 8 | 4 | 0 | 29 | 9999 | 9999 | 9999 | 9999 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
9 | 9 | 4 | 9999 | 9999 | 0 | 29 | 9999 | 9999 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
10 | 10 | 4 | 0 | 28 | 2.5 | 28 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
11 | 11 | 4 | 0 | 28 | 2.5 | 28 | 7 | 28 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999