## StudyCase
Case | LF_Method | Tolerance | Iteration limit | Initialization | System Freq | Earth Resistivity | Load | Reference bus | VoltageStart | Source Voltage BFS | AngleRef | Load Voltage Sentivity factor | LoadData
1 | 0 | 0.0001 | 500 | 0 | 60 | 100 | 0 | 1 | 1 | 0 | 0 | 0.75 | 0
Note on E1: hemanth: 0 - Flat Start 1 - Pre defined
Note on G1: Author: earth sentivity for computing the line impedance using carson's eq
Note on K1: 0- voltage data reference from db 1- voltage data from online data
Note on N1: Author: 0 - from db 1 - from real time feed (Not available for public)

## Nodes
BusNo | BusName | ZoneNo | Vnom (kVLL) | Vmin | Vmax
1 | Bus1 | 1 | 12.66 | 11.394 | 13.926
2 | Bus2 | 1 | 12.66 | 11.394 | 13.926
3 | Bus3 | 1 | 12.66 | 11.394 | 13.926
4 | Bus4 | 1 | 12.66 | 11.394 | 13.926
5 | Bus5 | 1 | 12.66 | 11.394 | 13.926
6 | Bus6 | 1 | 12.66 | 11.394 | 13.926
7 | Bus7 | 1 | 12.66 | 11.394 | 13.926
8 | Bus8 | 1 | 12.66 | 11.394 | 13.926
9 | Bus9 | 1 | 12.66 | 11.394 | 13.926
10 | Bus10 | 1 | 12.66 | 11.394 | 13.926
11 | Bus11 | 1 | 12.66 | 11.394 | 13.926
12 | Bus12 | 1 | 12.66 | 11.394 | 13.926
13 | Bus13 | 1 | 12.66 | 11.394 | 13.926
14 | Bus14 | 1 | 12.66 | 11.394 | 13.926
15 | Bus15 | 1 | 12.66 | 11.394 | 13.926
16 | Bus16 | 1 | 12.66 | 11.394 | 13.926
17 | Bus17 | 1 | 12.66 | 11.394 | 13.926
18 | Bus18 | 1 | 12.66 | 11.394 | 13.926
19 | Bus19 | 1 | 12.66 | 11.394 | 13.926
20 | Bus20 | 1 | 12.66 | 11.394 | 13.926
21 | Bus21 | 1 | 12.66 | 11.394 | 13.926
22 | Bus22 | 1 | 12.66 | 11.394 | 13.926
23 | Bus23 | 1 | 12.66 | 11.394 | 13.926
24 | Bus24 | 1 | 12.66 | 11.394 | 13.926
25 | Bus25 | 1 | 12.66 | 11.394 | 13.926
26 | Bus26 | 1 | 12.66 | 11.394 | 13.926
27 | Bus27 | 1 | 12.66 | 11.394 | 13.926
28 | Bus28 | 1 | 12.66 | 11.394 | 13.926
29 | Bus29 | 1 | 12.66 | 11.394 | 13.926
30 | Bus30 | 1 | 12.66 | 11.394 | 13.926
31 | Bus31 | 1 | 12.66 | 11.394 | 13.926
32 | Bus32 | 1 | 12.66 | 11.394 | 13.926
33 | Bus33 | 1 | 12.66 | 11.394 | 13.926
34 | Bus34 | 1 | 0.24 | 0.216 | 0.264
35 | Bus35 | 1 | 0.24 | 0.216 | 0.264
36 | Bus36 | 1 | 0.24 | 0.216 | 0.264
37 | Bus37 | 1 | 0.24 | 0.216 | 0.264
38 | Bus38 | 1 | 0.24 | 0.216 | 0.264
39 | Bus39 | 1 | 0.24 | 0.216 | 0.264
40 | Bus40 | 1 | 0.24 | 0.216 | 0.264
41 | Bus41 | 1 | 0.24 | 0.216 | 0.264
42 | Bus42 | 1 | 0.24 | 0.216 | 0.264
43 | Bus43 | 1 | 0.24 | 0.216 | 0.264
44 | Bus44 | 1 | 0.24 | 0.216 | 0.264
45 | Bus45 | 1 | 0.24 | 0.216 | 0.264
46 | Bus46 | 1 | 0.24 | 0.216 | 0.264
47 | Bus47 | 1 | 0.24 | 0.216 | 0.264
48 | Bus48 | 1 | 0.24 | 0.216 | 0.264
49 | Bus49 | 1 | 0.24 | 0.216 | 0.264
50 | Bus50 | 1 | 0.24 | 0.216 | 0.264
51 | Bus51 | 1 | 0.24 | 0.216 | 0.264
52 | Bus52 | 1 | 0.24 | 0.216 | 0.264
53 | Bus53 | 1 | 0.24 | 0.216 | 0.264
54 | Bus54 | 1 | 0.24 | 0.216 | 0.264
55 | Bus55 | 1 | 0.24 | 0.216 | 0.264
56 | Bus56 | 1 | 0.24 | 0.216 | 0.264
57 | Bus57 | 1 | 0.24 | 0.216 | 0.264
58 | Bus58 | 1 | 0.24 | 0.216 | 0.264
59 | Bus59 | 1 | 0.24 | 0.216 | 0.264
60 | Bus60 | 1 | 0.24 | 0.216 | 0.264
61 | Bus61 | 1 | 0.24 | 0.216 | 0.264
62 | Bus62 | 1 | 0.24 | 0.216 | 0.264
63 | Bus63 | 1 | 0.24 | 0.216 | 0.264
64 | Bus64 | 1 | 0.24 | 0.216 | 0.264
65 | Bus65 | 1 | 0.24 | 0.216 | 0.264
66 | Bus66 | 1 | 0.24 | 0.216 | 0.264
67 | Bus67 | 1 | 0.24 | 0.216 | 0.264
68 | Bus68 | 1 | 0.24 | 0.216 | 0.264
69 | Bus69 | 1 | 0.24 | 0.216 | 0.264
70 | Bus70 | 1 | 0.24 | 0.216 | 0.264
71 | Bus71 | 1 | 0.24 | 0.216 | 0.264
72 | Bus72 | 1 | 0.24 | 0.216 | 0.264
73 | Bus73 | 1 | 0.24 | 0.216 | 0.264
74 | Bus74 | 1 | 0.24 | 0.216 | 0.264
75 | Bus75 | 1 | 0.24 | 0.216 | 0.264
76 | Bus76 | 1 | 0.24 | 0.216 | 0.264
77 | Bus77 | 1 | 0.24 | 0.216 | 0.264
78 | Bus78 | 1 | 0.24 | 0.216 | 0.264
79 | Bus79 | 1 | 0.24 | 0.216 | 0.264
80 | Bus80 | 1 | 0.24 | 0.216 | 0.264
81 | Bus81 | 1 | 0.24 | 0.216 | 0.264
82 | Bus82 | 1 | 0.24 | 0.216 | 0.264
83 | Bus83 | 1 | 0.24 | 0.216 | 0.264
84 | Bus84 | 1 | 0.24 | 0.216 | 0.264
85 | Bus85 | 1 | 0.24 | 0.216 | 0.264
86 | Bus86 | 1 | 0.24 | 0.216 | 0.264
87 | Bus87 | 1 | 0.24 | 0.216 | 0.264
88 | Bus88 | 1 | 0.24 | 0.216 | 0.264
89 | Bus89 | 1 | 0.24 | 0.216 | 0.264
90 | Bus90 | 1 | 0.24 | 0.216 | 0.264
91 | Bus91 | 1 | 0.24 | 0.216 | 0.264
92 | Bus92 | 1 | 0.24 | 0.216 | 0.264
93 | Bus93 | 1 | 0.24 | 0.216 | 0.264
94 | Bus94 | 1 | 0.24 | 0.216 | 0.264
95 | Bus95 | 1 | 0.24 | 0.216 | 0.264
96 | Bus96 | 1 | 0.24 | 0.216 | 0.264
97 | Bus97 | 1 | 0.24 | 0.216 | 0.264
98 | Bus98 | 1 | 0.24 | 0.216 | 0.264
99 | Bus99 | 1 | 0.24 | 0.216 | 0.264
100 | Bus100 | 1 | 0.24 | 0.216 | 0.264
101 | Bus101 | 1 | 0.24 | 0.216 | 0.264
102 | Bus102 | 1 | 0.24 | 0.216 | 0.264
103 | Bus103 | 1 | 0.24 | 0.216 | 0.264
104 | Bus104 | 1 | 0.24 | 0.216 | 0.264
105 | Bus105 | 1 | 0.24 | 0.216 | 0.264
106 | Bus106 | 1 | 0.24 | 0.216 | 0.264
107 | Bus107 | 1 | 0.24 | 0.216 | 0.264
108 | Bus108 | 1 | 0.24 | 0.216 | 0.264
109 | Bus109 | 1 | 0.24 | 0.216 | 0.264
110 | Bus110 | 1 | 0.24 | 0.216 | 0.264
111 | Bus111 | 1 | 0.24 | 0.216 | 0.264
112 | Bus112 | 1 | 0.24 | 0.216 | 0.264
113 | Bus113 | 1 | 0.24 | 0.216 | 0.264
114 | Bus114 | 1 | 0.24 | 0.216 | 0.264
115 | Bus115 | 1 | 0.24 | 0.216 | 0.264
116 | Bus116 | 1 | 0.24 | 0.216 | 0.264
117 | Bus117 | 1 | 0.24 | 0.216 | 0.264
118 | Bus118 | 1 | 0.24 | 0.216 | 0.264
119 | Bus119 | 1 | 0.24 | 0.216 | 0.264
120 | Bus120 | 1 | 0.24 | 0.216 | 0.264
121 | Bus121 | 1 | 0.24 | 0.216 | 0.264
122 | Bus122 | 1 | 0.24 | 0.216 | 0.264
123 | Bus123 | 1 | 0.24 | 0.216 | 0.264
124 | Bus124 | 1 | 0.24 | 0.216 | 0.264
125 | Bus125 | 1 | 0.24 | 0.216 | 0.264
126 | Bus126 | 1 | 0.24 | 0.216 | 0.264
127 | Bus127 | 1 | 0.24 | 0.216 | 0.264
128 | Bus128 | 1 | 0.24 | 0.216 | 0.264
129 | Bus129 | 1 | 0.24 | 0.216 | 0.264
130 | Bus130 | 1 | 0.24 | 0.216 | 0.264
131 | Bus131 | 1 | 0.24 | 0.216 | 0.264
132 | Bus132 | 1 | 0.24 | 0.216 | 0.264
133 | Bus133 | 1 | 0.24 | 0.216 | 0.264
134 | Bus134 | 1 | 0.24 | 0.216 | 0.264
135 | Bus135 | 1 | 0.24 | 0.216 | 0.264
136 | Bus136 | 1 | 0.24 | 0.216 | 0.264
137 | Bus137 | 1 | 0.24 | 0.216 | 0.264
138 | Bus138 | 1 | 0.24 | 0.216 | 0.264
139 | Bus139 | 1 | 0.24 | 0.216 | 0.264
140 | Bus140 | 1 | 0.24 | 0.216 | 0.264
141 | Bus141 | 1 | 0.24 | 0.216 | 0.264
142 | Bus142 | 1 | 0.24 | 0.216 | 0.264
143 | Bus143 | 1 | 0.24 | 0.216 | 0.264
144 | Bus144 | 1 | 0.24 | 0.216 | 0.264
145 | Bus145 | 1 | 0.24 | 0.216 | 0.264
146 | Bus146 | 1 | 0.24 | 0.216 | 0.264
147 | Bus147 | 1 | 0.24 | 0.216 | 0.264
148 | Bus148 | 1 | 0.24 | 0.216 | 0.264
149 | Bus149 | 1 | 0.24 | 0.216 | 0.264
150 | Bus150 | 1 | 0.24 | 0.216 | 0.264
151 | Bus151 | 1 | 0.24 | 0.216 | 0.264
152 | Bus152 | 1 | 0.24 | 0.216 | 0.264
153 | Bus153 | 1 | 0.24 | 0.216 | 0.264
154 | Bus154 | 1 | 0.24 | 0.216 | 0.264
155 | Bus155 | 1 | 0.24 | 0.216 | 0.264
156 | Bus156 | 1 | 0.24 | 0.216 | 0.264
157 | Bus157 | 1 | 0.24 | 0.216 | 0.264
158 | Bus158 | 1 | 0.24 | 0.216 | 0.264
159 | Bus159 | 1 | 0.24 | 0.216 | 0.264
160 | Bus160 | 1 | 0.24 | 0.216 | 0.264
161 | Bus161 | 1 | 0.24 | 0.216 | 0.264
162 | Bus162 | 1 | 0.24 | 0.216 | 0.264
163 | Bus163 | 1 | 0.24 | 0.216 | 0.264
164 | Bus164 | 1 | 0.24 | 0.216 | 0.264
165 | Bus165 | 1 | 0.24 | 0.216 | 0.264
166 | Bus166 | 1 | 0.24 | 0.216 | 0.264
167 | Bus167 | 1 | 0.24 | 0.216 | 0.264
168 | Bus168 | 1 | 0.24 | 0.216 | 0.264
169 | Bus169 | 1 | 0.24 | 0.216 | 0.264
170 | Bus170 | 1 | 0.24 | 0.216 | 0.264
171 | Bus171 | 1 | 0.24 | 0.216 | 0.264
172 | Bus172 | 1 | 0.24 | 0.216 | 0.264
173 | Bus173 | 1 | 0.24 | 0.216 | 0.264
174 | Bus174 | 1 | 0.24 | 0.216 | 0.264
175 | Bus175 | 1 | 0.24 | 0.216 | 0.264
176 | Bus176 | 1 | 0.24 | 0.216 | 0.264
177 | Bus177 | 1 | 0.24 | 0.216 | 0.264
178 | Bus178 | 1 | 0.24 | 0.216 | 0.264
179 | Bus179 | 1 | 0.24 | 0.216 | 0.264
180 | Bus180 | 1 | 0.24 | 0.216 | 0.264
181 | Bus181 | 1 | 0.24 | 0.216 | 0.264
182 | Bus182 | 1 | 0.24 | 0.216 | 0.264
183 | Bus183 | 1 | 0.24 | 0.216 | 0.264
184 | Bus184 | 1 | 0.24 | 0.216 | 0.264
185 | Bus185 | 1 | 0.24 | 0.216 | 0.264
186 | Bus186 | 1 | 0.24 | 0.216 | 0.264
187 | Bus187 | 1 | 0.24 | 0.216 | 0.264
188 | Bus188 | 1 | 0.24 | 0.216 | 0.264
189 | Bus189 | 1 | 0.24 | 0.216 | 0.264
190 | Bus190 | 1 | 0.24 | 0.216 | 0.264
191 | Bus191 | 1 | 0.24 | 0.216 | 0.264
192 | Bus192 | 1 | 0.24 | 0.216 | 0.264
193 | Bus193 | 1 | 0.24 | 0.216 | 0.264
194 | Bus194 | 1 | 0.24 | 0.216 | 0.264
195 | Bus195 | 1 | 0.24 | 0.216 | 0.264
196 | Bus196 | 1 | 0.24 | 0.216 | 0.264
197 | Bus197 | 1 | 0.24 | 0.216 | 0.264
198 | Bus198 | 1 | 0.24 | 0.216 | 0.264
199 | Bus199 | 1 | 0.24 | 0.216 | 0.264
200 | Bus200 | 1 | 0.24 | 0.216 | 0.264
201 | Bus201 | 1 | 0.24 | 0.216 | 0.264
202 | Bus202 | 1 | 0.24 | 0.216 | 0.264
203 | Bus203 | 1 | 0.24 | 0.216 | 0.264
204 | Bus204 | 1 | 0.24 | 0.216 | 0.264
205 | Bus205 | 1 | 0.24 | 0.216 | 0.264
206 | Bus206 | 1 | 0.24 | 0.216 | 0.264
207 | Bus207 | 1 | 0.24 | 0.216 | 0.264
208 | Bus208 | 1 | 0.24 | 0.216 | 0.264
209 | Bus209 | 1 | 0.24 | 0.216 | 0.264
210 | Bus210 | 1 | 0.24 | 0.216 | 0.264
211 | Bus211 | 1 | 0.24 | 0.216 | 0.264
212 | Bus212 | 1 | 0.24 | 0.216 | 0.264
213 | Bus213 | 1 | 0.24 | 0.216 | 0.264
214 | Bus214 | 1 | 0.24 | 0.216 | 0.264
215 | Bus215 | 1 | 0.24 | 0.216 | 0.264
216 | Bus216 | 1 | 0.24 | 0.216 | 0.264
217 | Bus217 | 1 | 0.24 | 0.216 | 0.264
218 | Bus218 | 1 | 0.24 | 0.216 | 0.264
219 | Bus219 | 1 | 0.24 | 0.216 | 0.264
220 | Bus220 | 1 | 0.24 | 0.216 | 0.264
221 | Bus221 | 1 | 0.24 | 0.216 | 0.264
222 | Bus222 | 1 | 0.24 | 0.216 | 0.264
223 | Bus223 | 1 | 0.24 | 0.216 | 0.264
224 | Bus224 | 1 | 0.24 | 0.216 | 0.264
225 | Bus225 | 1 | 0.24 | 0.216 | 0.264
226 | Bus226 | 1 | 0.24 | 0.216 | 0.264
227 | Bus227 | 1 | 0.24 | 0.216 | 0.264
228 | Bus228 | 1 | 0.24 | 0.216 | 0.264
229 | Bus229 | 1 | 0.24 | 0.216 | 0.264
230 | Bus230 | 1 | 0.24 | 0.216 | 0.264
231 | Bus231 | 1 | 0.24 | 0.216 | 0.264
232 | Bus232 | 1 | 0.24 | 0.216 | 0.264
233 | Bus233 | 1 | 0.24 | 0.216 | 0.264
234 | Bus234 | 1 | 0.24 | 0.216 | 0.264
235 | Bus235 | 1 | 0.24 | 0.216 | 0.264
236 | Bus236 | 1 | 0.24 | 0.216 | 0.264
237 | Bus237 | 1 | 0.24 | 0.216 | 0.264
238 | Bus238 | 1 | 0.24 | 0.216 | 0.264
239 | Bus239 | 1 | 0.24 | 0.216 | 0.264
240 | Bus240 | 1 | 0.24 | 0.216 | 0.264
241 | Bus241 | 1 | 0.24 | 0.216 | 0.264
242 | Bus242 | 1 | 0.24 | 0.216 | 0.264
243 | Bus243 | 1 | 0.24 | 0.216 | 0.264
244 | Bus244 | 1 | 0.24 | 0.216 | 0.264
245 | Bus245 | 1 | 0.24 | 0.216 | 0.264
246 | Bus246 | 1 | 0.24 | 0.216 | 0.264
247 | Bus247 | 1 | 0.24 | 0.216 | 0.264
248 | Bus248 | 1 | 0.24 | 0.216 | 0.264
249 | Bus249 | 1 | 0.24 | 0.216 | 0.264
250 | Bus250 | 1 | 0.24 | 0.216 | 0.264
251 | Bus251 | 1 | 0.24 | 0.216 | 0.264
252 | Bus252 | 1 | 0.24 | 0.216 | 0.264
253 | Bus253 | 1 | 0.24 | 0.216 | 0.264
254 | Bus254 | 1 | 0.24 | 0.216 | 0.264
255 | Bus255 | 1 | 0.24 | 0.216 | 0.264
256 | Bus256 | 1 | 0.24 | 0.216 | 0.264
257 | Bus257 | 1 | 0.24 | 0.216 | 0.264
258 | Bus258 | 1 | 0.24 | 0.216 | 0.264
259 | Bus259 | 1 | 0.24 | 0.216 | 0.264
260 | Bus260 | 1 | 0.24 | 0.216 | 0.264
261 | Bus261 | 1 | 0.24 | 0.216 | 0.264
262 | Bus262 | 1 | 0.24 | 0.216 | 0.264
263 | Bus263 | 1 | 0.24 | 0.216 | 0.264
264 | Bus264 | 1 | 0.24 | 0.216 | 0.264
265 | Bus265 | 1 | 0.24 | 0.216 | 0.264
266 | Bus266 | 1 | 0.24 | 0.216 | 0.264
267 | Bus267 | 1 | 0.24 | 0.216 | 0.264
268 | Bus268 | 1 | 0.24 | 0.216 | 0.264
269 | Bus269 | 1 | 0.24 | 0.216 | 0.264
270 | Bus270 | 1 | 0.24 | 0.216 | 0.264
271 | Bus271 | 1 | 0.24 | 0.216 | 0.264
272 | Bus272 | 1 | 0.24 | 0.216 | 0.264
273 | Bus273 | 1 | 0.24 | 0.216 | 0.264
274 | Bus274 | 1 | 0.24 | 0.216 | 0.264
275 | Bus275 | 1 | 0.24 | 0.216 | 0.264
276 | Bus276 | 1 | 0.24 | 0.216 | 0.264
277 | Bus277 | 1 | 0.24 | 0.216 | 0.264
278 | Bus278 | 1 | 0.24 | 0.216 | 0.264
279 | Bus279 | 1 | 0.24 | 0.216 | 0.264
280 | Bus280 | 1 | 0.24 | 0.216 | 0.264
281 | Bus281 | 1 | 0.24 | 0.216 | 0.264
282 | Bus282 | 1 | 0.24 | 0.216 | 0.264
283 | Bus283 | 1 | 0.24 | 0.216 | 0.264
284 | Bus284 | 1 | 0.24 | 0.216 | 0.264
285 | Bus285 | 1 | 0.24 | 0.216 | 0.264
286 | Bus286 | 1 | 0.24 | 0.216 | 0.264
287 | Bus287 | 1 | 0.24 | 0.216 | 0.264
288 | Bus288 | 1 | 0.24 | 0.216 | 0.264
289 | Bus289 | 1 | 0.24 | 0.216 | 0.264
290 | Bus290 | 1 | 0.24 | 0.216 | 0.264
291 | Bus291 | 1 | 0.24 | 0.216 | 0.264
292 | Bus292 | 1 | 0.24 | 0.216 | 0.264
293 | Bus293 | 1 | 0.24 | 0.216 | 0.264
294 | Bus294 | 1 | 0.24 | 0.216 | 0.264
295 | Bus295 | 1 | 0.24 | 0.216 | 0.264
296 | Bus296 | 1 | 0.24 | 0.216 | 0.264
297 | Bus297 | 1 | 0.24 | 0.216 | 0.264
298 | Bus298 | 1 | 0.24 | 0.216 | 0.264
299 | Bus299 | 1 | 0.24 | 0.216 | 0.264
300 | Bus300 | 1 | 0.24 | 0.216 | 0.264
301 | Bus301 | 1 | 0.24 | 0.216 | 0.264
302 | Bus302 | 1 | 0.24 | 0.216 | 0.264
303 | Bus303 | 1 | 0.24 | 0.216 | 0.264
304 | Bus304 | 1 | 0.24 | 0.216 | 0.264
305 | Bus305 | 1 | 0.24 | 0.216 | 0.264
306 | Bus306 | 1 | 0.24 | 0.216 | 0.264
307 | Bus307 | 1 | 0.24 | 0.216 | 0.264
308 | Bus308 | 1 | 0.24 | 0.216 | 0.264
309 | Bus309 | 1 | 0.24 | 0.216 | 0.264
310 | Bus310 | 1 | 0.24 | 0.216 | 0.264
311 | Bus311 | 1 | 0.24 | 0.216 | 0.264
312 | Bus312 | 1 | 0.24 | 0.216 | 0.264
313 | Bus313 | 1 | 0.24 | 0.216 | 0.264
314 | Bus314 | 1 | 0.24 | 0.216 | 0.264
315 | Bus315 | 1 | 0.24 | 0.216 | 0.264
316 | Bus316 | 1 | 0.24 | 0.216 | 0.264
317 | Bus317 | 1 | 0.24 | 0.216 | 0.264
318 | Bus318 | 1 | 0.24 | 0.216 | 0.264
319 | Bus319 | 1 | 0.24 | 0.216 | 0.264
320 | Bus320 | 1 | 0.24 | 0.216 | 0.264
321 | Bus321 | 1 | 0.24 | 0.216 | 0.264
322 | Bus322 | 1 | 0.24 | 0.216 | 0.264
323 | Bus323 | 1 | 0.24 | 0.216 | 0.264
324 | Bus324 | 1 | 0.24 | 0.216 | 0.264
325 | Bus325 | 1 | 0.24 | 0.216 | 0.264
326 | Bus326 | 1 | 0.24 | 0.216 | 0.264
327 | Bus327 | 1 | 0.24 | 0.216 | 0.264
328 | Bus328 | 1 | 0.24 | 0.216 | 0.264
329 | Bus329 | 1 | 0.24 | 0.216 | 0.264
330 | Bus330 | 1 | 0.24 | 0.216 | 0.264
331 | Bus331 | 1 | 0.24 | 0.216 | 0.264
332 | Bus332 | 1 | 0.24 | 0.216 | 0.264
333 | Bus333 | 1 | 0.24 | 0.216 | 0.264
334 | Bus334 | 1 | 0.24 | 0.216 | 0.264
335 | Bus335 | 1 | 0.24 | 0.216 | 0.264
336 | Bus336 | 1 | 0.24 | 0.216 | 0.264
337 | Bus337 | 1 | 0.24 | 0.216 | 0.264
338 | Bus338 | 1 | 0.24 | 0.216 | 0.264
339 | Bus339 | 1 | 0.24 | 0.216 | 0.264
340 | Bus340 | 1 | 0.24 | 0.216 | 0.264
341 | Bus341 | 1 | 0.24 | 0.216 | 0.264
342 | Bus342 | 1 | 0.24 | 0.216 | 0.264
343 | Bus343 | 1 | 0.24 | 0.216 | 0.264
344 | Bus344 | 1 | 0.24 | 0.216 | 0.264
345 | Bus345 | 1 | 0.24 | 0.216 | 0.264
346 | Bus346 | 1 | 0.24 | 0.216 | 0.264
347 | Bus347 | 1 | 0.24 | 0.216 | 0.264
348 | Bus348 | 1 | 0.24 | 0.216 | 0.264
349 | Bus349 | 1 | 0.24 | 0.216 | 0.264
350 | Bus350 | 1 | 0.24 | 0.216 | 0.264
351 | Bus351 | 1 | 0.24 | 0.216 | 0.264
352 | Bus352 | 1 | 0.24 | 0.216 | 0.264
353 | Bus353 | 1 | 0.24 | 0.216 | 0.264
354 | Bus354 | 1 | 0.24 | 0.216 | 0.264
355 | Bus355 | 1 | 0.24 | 0.216 | 0.264
356 | Bus356 | 1 | 0.24 | 0.216 | 0.264
357 | Bus357 | 1 | 0.24 | 0.216 | 0.264
358 | Bus358 | 1 | 0.24 | 0.216 | 0.264
359 | Bus359 | 1 | 0.24 | 0.216 | 0.264
360 | Bus360 | 1 | 0.24 | 0.216 | 0.264
361 | Bus361 | 1 | 0.24 | 0.216 | 0.264
362 | Bus362 | 1 | 0.24 | 0.216 | 0.264
363 | Bus363 | 1 | 0.24 | 0.216 | 0.264
364 | Bus364 | 1 | 0.24 | 0.216 | 0.264
365 | Bus365 | 1 | 0.24 | 0.216 | 0.264
366 | Bus366 | 1 | 0.24 | 0.216 | 0.264
367 | Bus367 | 1 | 0.24 | 0.216 | 0.264
368 | Bus368 | 1 | 0.24 | 0.216 | 0.264
369 | Bus369 | 1 | 0.24 | 0.216 | 0.264
370 | Bus370 | 1 | 0.24 | 0.216 | 0.264
371 | Bus371 | 1 | 0.24 | 0.216 | 0.264
372 | Bus372 | 1 | 0.24 | 0.216 | 0.264
373 | Bus373 | 1 | 0.24 | 0.216 | 0.264
374 | Bus374 | 1 | 0.24 | 0.216 | 0.264
375 | Bus375 | 1 | 0.24 | 0.216 | 0.264
376 | Bus376 | 1 | 0.24 | 0.216 | 0.264
377 | Bus377 | 1 | 0.24 | 0.216 | 0.264
378 | Bus378 | 1 | 0.24 | 0.216 | 0.264
379 | Bus379 | 1 | 0.24 | 0.216 | 0.264
380 | Bus380 | 1 | 0.24 | 0.216 | 0.264
381 | Bus381 | 1 | 0.24 | 0.216 | 0.264
382 | Bus382 | 1 | 0.24 | 0.216 | 0.264
383 | Bus383 | 1 | 0.24 | 0.216 | 0.264
384 | Bus384 | 1 | 0.24 | 0.216 | 0.264
385 | Bus385 | 1 | 0.24 | 0.216 | 0.264
386 | Bus386 | 1 | 0.24 | 0.216 | 0.264
387 | Bus387 | 1 | 0.24 | 0.216 | 0.264
388 | Bus388 | 1 | 0.24 | 0.216 | 0.264
389 | Bus389 | 1 | 0.24 | 0.216 | 0.264
390 | Bus390 | 1 | 0.24 | 0.216 | 0.264
391 | Bus391 | 1 | 0.24 | 0.216 | 0.264
392 | Bus392 | 1 | 0.24 | 0.216 | 0.264
393 | Bus393 | 1 | 0.24 | 0.216 | 0.264
394 | Bus394 | 1 | 0.24 | 0.216 | 0.264
395 | Bus395 | 1 | 0.24 | 0.216 | 0.264
396 | Bus396 | 1 | 0.24 | 0.216 | 0.264
397 | Bus397 | 1 | 0.24 | 0.216 | 0.264
398 | Bus398 | 1 | 0.24 | 0.216 | 0.264
399 | Bus399 | 1 | 0.24 | 0.216 | 0.264
400 | Bus400 | 1 | 0.24 | 0.216 | 0.264
401 | Bus401 | 1 | 0.24 | 0.216 | 0.264
402 | Bus402 | 1 | 0.24 | 0.216 | 0.264
403 | Bus403 | 1 | 0.24 | 0.216 | 0.264
404 | Bus404 | 1 | 0.24 | 0.216 | 0.264
405 | Bus405 | 1 | 0.24 | 0.216 | 0.264
406 | Bus406 | 1 | 0.24 | 0.216 | 0.264
407 | Bus407 | 1 | 0.24 | 0.216 | 0.264
408 | Bus408 | 1 | 0.24 | 0.216 | 0.264
409 | Bus409 | 1 | 0.24 | 0.216 | 0.264
410 | Bus410 | 1 | 0.24 | 0.216 | 0.264
411 | Bus411 | 1 | 0.24 | 0.216 | 0.264
412 | Bus412 | 1 | 0.24 | 0.216 | 0.264
413 | Bus413 | 1 | 0.24 | 0.216 | 0.264
414 | Bus414 | 1 | 0.24 | 0.216 | 0.264
415 | Bus415 | 1 | 0.24 | 0.216 | 0.264
416 | Bus416 | 1 | 0.24 | 0.216 | 0.264
417 | Bus417 | 1 | 0.24 | 0.216 | 0.264
418 | Bus418 | 1 | 0.24 | 0.216 | 0.264
419 | Bus419 | 1 | 0.24 | 0.216 | 0.264
420 | Bus420 | 1 | 0.24 | 0.216 | 0.264
421 | Bus421 | 1 | 0.24 | 0.216 | 0.264
422 | Bus422 | 1 | 0.24 | 0.216 | 0.264
423 | Bus423 | 1 | 0.24 | 0.216 | 0.264
424 | Bus424 | 1 | 0.24 | 0.216 | 0.264
425 | Bus425 | 1 | 0.24 | 0.216 | 0.264
426 | Bus426 | 1 | 0.24 | 0.216 | 0.264
427 | Bus427 | 1 | 0.24 | 0.216 | 0.264
428 | Bus428 | 1 | 0.24 | 0.216 | 0.264
429 | Bus429 | 1 | 0.24 | 0.216 | 0.264
430 | Bus430 | 1 | 0.24 | 0.216 | 0.264
431 | Bus431 | 1 | 0.24 | 0.216 | 0.264
432 | Bus432 | 1 | 0.24 | 0.216 | 0.264
433 | Bus433 | 1 | 0.24 | 0.216 | 0.264
434 | Bus434 | 1 | 0.24 | 0.216 | 0.264
435 | Bus435 | 1 | 0.24 | 0.216 | 0.264
436 | Bus436 | 1 | 0.24 | 0.216 | 0.264
437 | Bus437 | 1 | 0.24 | 0.216 | 0.264
438 | Bus438 | 1 | 0.24 | 0.216 | 0.264
439 | Bus439 | 1 | 0.24 | 0.216 | 0.264
440 | Bus440 | 1 | 0.24 | 0.216 | 0.264
441 | Bus441 | 1 | 0.24 | 0.216 | 0.264
442 | Bus442 | 1 | 0.24 | 0.216 | 0.264
443 | Bus443 | 1 | 0.24 | 0.216 | 0.264
444 | Bus444 | 1 | 0.24 | 0.216 | 0.264
445 | Bus445 | 1 | 0.24 | 0.216 | 0.264
446 | Bus446 | 1 | 0.24 | 0.216 | 0.264
447 | Bus447 | 1 | 0.24 | 0.216 | 0.264
448 | Bus448 | 1 | 0.24 | 0.216 | 0.264
449 | Bus449 | 1 | 0.24 | 0.216 | 0.264
450 | Bus450 | 1 | 0.24 | 0.216 | 0.264
451 | Bus451 | 1 | 0.24 | 0.216 | 0.264
452 | Bus452 | 1 | 0.24 | 0.216 | 0.264
453 | Bus453 | 1 | 0.24 | 0.216 | 0.264
454 | Bus454 | 1 | 0.24 | 0.216 | 0.264
455 | Bus455 | 1 | 0.24 | 0.216 | 0.264
456 | Bus456 | 1 | 0.24 | 0.216 | 0.264
457 | Bus457 | 1 | 0.24 | 0.216 | 0.264
458 | Bus458 | 1 | 0.24 | 0.216 | 0.264
459 | Bus459 | 1 | 0.24 | 0.216 | 0.264
460 | Bus460 | 1 | 0.24 | 0.216 | 0.264
461 | Bus461 | 1 | 0.24 | 0.216 | 0.264
462 | Bus462 | 1 | 0.24 | 0.216 | 0.264
463 | Bus463 | 1 | 0.24 | 0.216 | 0.264
464 | Bus464 | 1 | 0.24 | 0.216 | 0.264
465 | Bus465 | 1 | 0.24 | 0.216 | 0.264
466 | Bus466 | 1 | 0.24 | 0.216 | 0.264
467 | Bus467 | 1 | 0.24 | 0.216 | 0.264
468 | Bus468 | 1 | 0.24 | 0.216 | 0.264
469 | Bus469 | 1 | 0.24 | 0.216 | 0.264
470 | Bus470 | 1 | 0.24 | 0.216 | 0.264
471 | Bus471 | 1 | 0.24 | 0.216 | 0.264
472 | Bus472 | 1 | 0.24 | 0.216 | 0.264
473 | Bus473 | 1 | 0.24 | 0.216 | 0.264
474 | Bus474 | 1 | 0.24 | 0.216 | 0.264
475 | Bus475 | 1 | 0.24 | 0.216 | 0.264
476 | Bus476 | 1 | 0.24 | 0.216 | 0.264
477 | Bus477 | 1 | 0.24 | 0.216 | 0.264
478 | Bus478 | 1 | 0.24 | 0.216 | 0.264
479 | Bus479 | 1 | 0.24 | 0.216 | 0.264
480 | Bus480 | 1 | 0.24 | 0.216 | 0.264
481 | Bus481 | 1 | 0.24 | 0.216 | 0.264
482 | Bus482 | 1 | 0.24 | 0.216 | 0.264
483 | Bus483 | 1 | 0.24 | 0.216 | 0.264
484 | Bus484 | 1 | 0.24 | 0.216 | 0.264
485 | Bus485 | 1 | 0.24 | 0.216 | 0.264
486 | Bus486 | 1 | 0.24 | 0.216 | 0.264
487 | Bus487 | 1 | 0.24 | 0.216 | 0.264
488 | Bus488 | 1 | 0.24 | 0.216 | 0.264
489 | Bus489 | 1 | 0.24 | 0.216 | 0.264
490 | Bus490 | 1 | 0.24 | 0.216 | 0.264
491 | Bus491 | 1 | 0.24 | 0.216 | 0.264
492 | Bus492 | 1 | 0.24 | 0.216 | 0.264
493 | Bus493 | 1 | 0.24 | 0.216 | 0.264
494 | Bus494 | 1 | 0.24 | 0.216 | 0.264
495 | Bus495 | 1 | 0.24 | 0.216 | 0.264
496 | Bus496 | 1 | 0.24 | 0.216 | 0.264
497 | Bus497 | 1 | 0.24 | 0.216 | 0.264
498 | Bus498 | 1 | 0.24 | 0.216 | 0.264
499 | Bus499 | 1 | 0.24 | 0.216 | 0.264
500 | Bus500 | 1 | 0.24 | 0.216 | 0.264
501 | Bus501 | 1 | 0.24 | 0.216 | 0.264
502 | Bus502 | 1 | 0.24 | 0.216 | 0.264
503 | Bus503 | 1 | 0.24 | 0.216 | 0.264
504 | Bus504 | 1 | 0.24 | 0.216 | 0.264
505 | Bus505 | 1 | 0.24 | 0.216 | 0.264
506 | Bus506 | 1 | 0.24 | 0.216 | 0.264
507 | Bus507 | 1 | 0.24 | 0.216 | 0.264
508 | Bus508 | 1 | 0.24 | 0.216 | 0.264
509 | Bus509 | 1 | 0.24 | 0.216 | 0.264
510 | Bus510 | 1 | 0.24 | 0.216 | 0.264
511 | Bus511 | 1 | 0.24 | 0.216 | 0.264
512 | Bus512 | 1 | 0.24 | 0.216 | 0.264
513 | Bus513 | 1 | 0.24 | 0.216 | 0.264
514 | Bus514 | 1 | 0.24 | 0.216 | 0.264
515 | Bus515 | 1 | 0.24 | 0.216 | 0.264
516 | Bus516 | 1 | 0.24 | 0.216 | 0.264
517 | Bus517 | 1 | 0.24 | 0.216 | 0.264
518 | Bus518 | 1 | 0.24 | 0.216 | 0.264
519 | Bus519 | 1 | 0.24 | 0.216 | 0.264
520 | Bus520 | 1 | 0.24 | 0.216 | 0.264
521 | Bus521 | 1 | 0.24 | 0.216 | 0.264
522 | Bus522 | 1 | 0.24 | 0.216 | 0.264
523 | Bus523 | 1 | 0.24 | 0.216 | 0.264
524 | Bus524 | 1 | 0.24 | 0.216 | 0.264
525 | Bus525 | 1 | 0.24 | 0.216 | 0.264
526 | Bus526 | 1 | 0.24 | 0.216 | 0.264
527 | Bus527 | 1 | 0.24 | 0.216 | 0.264
528 | Bus528 | 1 | 0.24 | 0.216 | 0.264
529 | Bus529 | 1 | 0.24 | 0.216 | 0.264
530 | Bus530 | 1 | 0.24 | 0.216 | 0.264
531 | Bus531 | 1 | 0.24 | 0.216 | 0.264
532 | Bus532 | 1 | 0.24 | 0.216 | 0.264
533 | Bus533 | 1 | 0.24 | 0.216 | 0.264
534 | Bus534 | 1 | 0.24 | 0.216 | 0.264
535 | Bus535 | 1 | 0.24 | 0.216 | 0.264
536 | Bus536 | 1 | 0.24 | 0.216 | 0.264
537 | Bus537 | 1 | 0.24 | 0.216 | 0.264
538 | Bus538 | 1 | 0.24 | 0.216 | 0.264
539 | Bus539 | 1 | 0.24 | 0.216 | 0.264
540 | Bus540 | 1 | 0.24 | 0.216 | 0.264
541 | Bus541 | 1 | 0.24 | 0.216 | 0.264
542 | Bus542 | 1 | 0.24 | 0.216 | 0.264
543 | Bus543 | 1 | 0.24 | 0.216 | 0.264
544 | Bus544 | 1 | 0.24 | 0.216 | 0.264
545 | Bus545 | 1 | 0.24 | 0.216 | 0.264
546 | Bus546 | 1 | 0.24 | 0.216 | 0.264
547 | Bus547 | 1 | 0.24 | 0.216 | 0.264
548 | Bus548 | 1 | 0.24 | 0.216 | 0.264
549 | Bus549 | 1 | 0.24 | 0.216 | 0.264
550 | Bus550 | 1 | 0.24 | 0.216 | 0.264
551 | Bus551 | 1 | 0.24 | 0.216 | 0.264
552 | Bus552 | 1 | 0.24 | 0.216 | 0.264
553 | Bus553 | 1 | 0.24 | 0.216 | 0.264
554 | Bus554 | 1 | 0.24 | 0.216 | 0.264
555 | Bus555 | 1 | 0.24 | 0.216 | 0.264
556 | Bus556 | 1 | 0.24 | 0.216 | 0.264
557 | Bus557 | 1 | 0.24 | 0.216 | 0.264
558 | Bus558 | 1 | 0.24 | 0.216 | 0.264
559 | Bus559 | 1 | 0.24 | 0.216 | 0.264
560 | Bus560 | 1 | 0.24 | 0.216 | 0.264
561 | Bus561 | 1 | 0.24 | 0.216 | 0.264
562 | Bus562 | 1 | 0.24 | 0.216 | 0.264
563 | Bus563 | 1 | 0.24 | 0.216 | 0.264
564 | Bus564 | 1 | 0.24 | 0.216 | 0.264
565 | Bus565 | 1 | 0.24 | 0.216 | 0.264
566 | Bus566 | 1 | 0.24 | 0.216 | 0.264
567 | Bus567 | 1 | 0.24 | 0.216 | 0.264
568 | Bus568 | 1 | 0.24 | 0.216 | 0.264
569 | Bus569 | 1 | 0.24 | 0.216 | 0.264
570 | Bus570 | 1 | 0.24 | 0.216 | 0.264
571 | Bus571 | 1 | 0.24 | 0.216 | 0.264
572 | Bus572 | 1 | 0.24 | 0.216 | 0.264
573 | Bus573 | 1 | 0.24 | 0.216 | 0.264
574 | Bus574 | 1 | 0.24 | 0.216 | 0.264
575 | Bus575 | 1 | 0.24 | 0.216 | 0.264
576 | Bus576 | 1 | 0.24 | 0.216 | 0.264
577 | Bus577 | 1 | 0.24 | 0.216 | 0.264
578 | Bus578 | 1 | 0.24 | 0.216 | 0.264
579 | Bus579 | 1 | 0.24 | 0.216 | 0.264
580 | Bus580 | 1 | 0.24 | 0.216 | 0.264
581 | Bus581 | 1 | 0.24 | 0.216 | 0.264
582 | Bus582 | 1 | 0.24 | 0.216 | 0.264
583 | Bus583 | 1 | 0.24 | 0.216 | 0.264
584 | Bus584 | 1 | 0.24 | 0.216 | 0.264
585 | Bus585 | 1 | 0.24 | 0.216 | 0.264
586 | Bus586 | 1 | 0.24 | 0.216 | 0.264
587 | Bus587 | 1 | 0.24 | 0.216 | 0.264
588 | Bus588 | 1 | 0.24 | 0.216 | 0.264
589 | Bus589 | 1 | 0.24 | 0.216 | 0.264
590 | Bus590 | 1 | 0.24 | 0.216 | 0.264
591 | Bus591 | 1 | 0.24 | 0.216 | 0.264
592 | Bus592 | 1 | 0.24 | 0.216 | 0.264
593 | Bus593 | 1 | 0.24 | 0.216 | 0.264
594 | Bus594 | 1 | 0.24 | 0.216 | 0.264
595 | Bus595 | 1 | 0.24 | 0.216 | 0.264
596 | Bus596 | 1 | 0.24 | 0.216 | 0.264
597 | Bus597 | 1 | 0.24 | 0.216 | 0.264
598 | Bus598 | 1 | 0.24 | 0.216 | 0.264
599 | Bus599 | 1 | 0.24 | 0.216 | 0.264
600 | Bus600 | 1 | 0.24 | 0.216 | 0.264
601 | Bus601 | 1 | 0.24 | 0.216 | 0.264
602 | Bus602 | 1 | 0.24 | 0.216 | 0.264
603 | Bus603 | 1 | 0.24 | 0.216 | 0.264
604 | Bus604 | 1 | 0.24 | 0.216 | 0.264
605 | Bus605 | 1 | 0.24 | 0.216 | 0.264
606 | Bus606 | 1 | 0.24 | 0.216 | 0.264
607 | Bus607 | 1 | 0.24 | 0.216 | 0.264
608 | Bus608 | 1 | 0.24 | 0.216 | 0.264
609 | Bus609 | 1 | 0.24 | 0.216 | 0.264
610 | Bus610 | 1 | 0.24 | 0.216 | 0.264
611 | Bus611 | 1 | 0.24 | 0.216 | 0.264
612 | Bus612 | 1 | 0.24 | 0.216 | 0.264
613 | Bus613 | 1 | 0.24 | 0.216 | 0.264
614 | Bus614 | 1 | 0.24 | 0.216 | 0.264
615 | Bus615 | 1 | 0.24 | 0.216 | 0.264
616 | Bus616 | 1 | 0.24 | 0.216 | 0.264
617 | Bus617 | 1 | 0.24 | 0.216 | 0.264
618 | Bus618 | 1 | 0.24 | 0.216 | 0.264
619 | Bus619 | 1 | 0.24 | 0.216 | 0.264
620 | Bus620 | 1 | 0.24 | 0.216 | 0.264
621 | Bus621 | 1 | 0.24 | 0.216 | 0.264
622 | Bus622 | 1 | 0.24 | 0.216 | 0.264
623 | Bus623 | 1 | 0.24 | 0.216 | 0.264
624 | Bus624 | 1 | 0.24 | 0.216 | 0.264
625 | Bus625 | 1 | 0.24 | 0.216 | 0.264
626 | Bus626 | 1 | 0.24 | 0.216 | 0.264
627 | Bus627 | 1 | 0.24 | 0.216 | 0.264
628 | Bus628 | 1 | 0.24 | 0.216 | 0.264
629 | Bus629 | 1 | 0.24 | 0.216 | 0.264
630 | Bus630 | 1 | 0.24 | 0.216 | 0.264
631 | Bus631 | 1 | 0.24 | 0.216 | 0.264
632 | Bus632 | 1 | 0.24 | 0.216 | 0.264
633 | Bus633 | 1 | 0.24 | 0.216 | 0.264
634 | Bus634 | 1 | 0.24 | 0.216 | 0.264
635 | Bus635 | 1 | 0.24 | 0.216 | 0.264
636 | Bus636 | 1 | 0.24 | 0.216 | 0.264
637 | Bus637 | 1 | 0.24 | 0.216 | 0.264
638 | Bus638 | 1 | 0.24 | 0.216 | 0.264
639 | Bus639 | 1 | 0.24 | 0.216 | 0.264
640 | Bus640 | 1 | 0.24 | 0.216 | 0.264
641 | Bus641 | 1 | 0.24 | 0.216 | 0.264
642 | Bus642 | 1 | 0.24 | 0.216 | 0.264
643 | Bus643 | 1 | 0.24 | 0.216 | 0.264
644 | Bus644 | 1 | 0.24 | 0.216 | 0.264
645 | Bus645 | 1 | 0.24 | 0.216 | 0.264
646 | Bus646 | 1 | 0.24 | 0.216 | 0.264
647 | Bus647 | 1 | 0.24 | 0.216 | 0.264
648 | Bus648 | 1 | 0.24 | 0.216 | 0.264
649 | Bus649 | 1 | 0.24 | 0.216 | 0.264
650 | Bus650 | 1 | 0.24 | 0.216 | 0.264
651 | Bus651 | 1 | 0.24 | 0.216 | 0.264
652 | Bus652 | 1 | 0.24 | 0.216 | 0.264
653 | Bus653 | 1 | 0.24 | 0.216 | 0.264
654 | Bus654 | 1 | 0.24 | 0.216 | 0.264
655 | Bus655 | 1 | 0.24 | 0.216 | 0.264
656 | Bus656 | 1 | 0.24 | 0.216 | 0.264
657 | Bus657 | 1 | 0.24 | 0.216 | 0.264
658 | Bus658 | 1 | 0.24 | 0.216 | 0.264
659 | Bus659 | 1 | 0.24 | 0.216 | 0.264
660 | Bus660 | 1 | 0.24 | 0.216 | 0.264
661 | Bus661 | 1 | 0.24 | 0.216 | 0.264
662 | Bus662 | 1 | 0.24 | 0.216 | 0.264
663 | Bus663 | 1 | 0.24 | 0.216 | 0.264
664 | Bus664 | 1 | 0.24 | 0.216 | 0.264
665 | Bus665 | 1 | 0.24 | 0.216 | 0.264
666 | Bus666 | 1 | 0.24 | 0.216 | 0.264
667 | Bus667 | 1 | 0.24 | 0.216 | 0.264
668 | Bus668 | 1 | 0.24 | 0.216 | 0.264
669 | Bus669 | 1 | 0.24 | 0.216 | 0.264
670 | Bus670 | 1 | 0.24 | 0.216 | 0.264
671 | Bus671 | 1 | 0.24 | 0.216 | 0.264
672 | Bus672 | 1 | 0.24 | 0.216 | 0.264
673 | Bus673 | 1 | 0.24 | 0.216 | 0.264
674 | Bus674 | 1 | 0.24 | 0.216 | 0.264
675 | Bus675 | 1 | 0.24 | 0.216 | 0.264
676 | Bus676 | 1 | 0.24 | 0.216 | 0.264
677 | Bus677 | 1 | 0.24 | 0.216 | 0.264
678 | Bus678 | 1 | 0.24 | 0.216 | 0.264
679 | Bus679 | 1 | 0.24 | 0.216 | 0.264
680 | Bus680 | 1 | 0.24 | 0.216 | 0.264
681 | Bus681 | 1 | 0.24 | 0.216 | 0.264
682 | Bus682 | 1 | 0.24 | 0.216 | 0.264
683 | Bus683 | 1 | 0.24 | 0.216 | 0.264
684 | Bus684 | 1 | 0.24 | 0.216 | 0.264
685 | Bus685 | 1 | 0.24 | 0.216 | 0.264
686 | Bus686 | 1 | 0.24 | 0.216 | 0.264
687 | Bus687 | 1 | 0.24 | 0.216 | 0.264
688 | Bus688 | 1 | 0.24 | 0.216 | 0.264
689 | Bus689 | 1 | 0.24 | 0.216 | 0.264
690 | Bus690 | 1 | 0.24 | 0.216 | 0.264
691 | Bus691 | 1 | 0.24 | 0.216 | 0.264
692 | Bus692 | 1 | 0.24 | 0.216 | 0.264
693 | Bus693 | 1 | 0.24 | 0.216 | 0.264
694 | Bus694 | 1 | 0.24 | 0.216 | 0.264
695 | Bus695 | 1 | 0.24 | 0.216 | 0.264
696 | Bus696 | 1 | 0.24 | 0.216 | 0.264
697 | Bus697 | 1 | 0.24 | 0.216 | 0.264
698 | Bus698 | 1 | 0.24 | 0.216 | 0.264
699 | Bus699 | 1 | 0.24 | 0.216 | 0.264
700 | Bus700 | 1 | 0.24 | 0.216 | 0.264
701 | Bus701 | 1 | 0.24 | 0.216 | 0.264
702 | Bus702 | 1 | 0.24 | 0.216 | 0.264
703 | Bus703 | 1 | 0.24 | 0.216 | 0.264
704 | Bus704 | 1 | 0.24 | 0.216 | 0.264
705 | Bus705 | 1 | 0.24 | 0.216 | 0.264
706 | Bus706 | 1 | 0.24 | 0.216 | 0.264
707 | Bus707 | 1 | 0.24 | 0.216 | 0.264
708 | Bus708 | 1 | 0.24 | 0.216 | 0.264
709 | Bus709 | 1 | 0.24 | 0.216 | 0.264
710 | Bus710 | 1 | 0.24 | 0.216 | 0.264
711 | Bus711 | 1 | 0.24 | 0.216 | 0.264
712 | Bus712 | 1 | 0.24 | 0.216 | 0.264
713 | Bus713 | 1 | 0.24 | 0.216 | 0.264
714 | Bus714 | 1 | 0.24 | 0.216 | 0.264
715 | Bus715 | 1 | 0.24 | 0.216 | 0.264
716 | Bus716 | 1 | 0.24 | 0.216 | 0.264
717 | Bus717 | 1 | 0.24 | 0.216 | 0.264
718 | Bus718 | 1 | 0.24 | 0.216 | 0.264
719 | Bus719 | 1 | 0.24 | 0.216 | 0.264
720 | Bus720 | 1 | 0.24 | 0.216 | 0.264
721 | Bus721 | 1 | 0.24 | 0.216 | 0.264
722 | Bus722 | 1 | 0.24 | 0.216 | 0.264
723 | Bus723 | 1 | 0.24 | 0.216 | 0.264
724 | Bus724 | 1 | 0.24 | 0.216 | 0.264
725 | Bus725 | 1 | 0.24 | 0.216 | 0.264
726 | Bus726 | 1 | 0.24 | 0.216 | 0.264
727 | Bus727 | 1 | 0.24 | 0.216 | 0.264
728 | Bus728 | 1 | 0.24 | 0.216 | 0.264
729 | Bus729 | 1 | 0.24 | 0.216 | 0.264
730 | Bus730 | 1 | 0.24 | 0.216 | 0.264

## Branch
BranchNo | FromNode | ToNodeB | Length (ft) | Config | Status
1 | 1 | 2 | 5280 | 500 | 1
2 | 2 | 3 | 5280 | 501 | 1
3 | 2 | 19 | 5280 | 502 | 1
4 | 3 | 4 | 5280 | 503 | 1
5 | 3 | 23 | 5280 | 504 | 1
6 | 4 | 5 | 5280 | 505 | 1
7 | 5 | 6 | 5280 | 506 | 1
8 | 6 | 7 | 5280 | 507 | 1
9 | 6 | 26 | 5280 | 508 | 1
10 | 7 | 8 | 5280 | 509 | 1
11 | 8 | 9 | 5280 | 510 | 1
12 | 9 | 10 | 5280 | 511 | 1
13 | 10 | 11 | 5280 | 512 | 1
14 | 11 | 12 | 5280 | 513 | 1
15 | 12 | 13 | 5280 | 514 | 1
16 | 13 | 14 | 5280 | 515 | 1
17 | 14 | 15 | 5280 | 516 | 1
18 | 15 | 16 | 5280 | 517 | 1
19 | 16 | 17 | 5280 | 518 | 1
20 | 17 | 18 | 5280 | 519 | 1
21 | 19 | 20 | 5280 | 520 | 1
22 | 20 | 21 | 5280 | 521 | 1
23 | 21 | 22 | 5280 | 522 | 1
24 | 23 | 24 | 5280 | 523 | 1
25 | 24 | 25 | 5280 | 524 | 1
26 | 26 | 27 | 5280 | 525 | 1
27 | 27 | 28 | 5280 | 526 | 1
28 | 28 | 29 | 5280 | 527 | 1
29 | 29 | 30 | 5280 | 528 | 1
30 | 30 | 31 | 5280 | 529 | 1
31 | 31 | 32 | 5280 | 530 | 1
32 | 32 | 33 | 5280 | 531 | 1
33 | 34 | 35 | 5280 | 532 | 1
34 | 35 | 41 | 5280 | 533 | 1
35 | 35 | 47 | 5280 | 534 | 1
36 | 35 | 36 | 5280 | 535 | 1
37 | 36 | 42 | 5280 | 536 | 1
38 | 36 | 48 | 5280 | 537 | 1
39 | 36 | 37 | 5280 | 538 | 1
40 | 37 | 43 | 5280 | 539 | 1
41 | 37 | 49 | 5280 | 540 | 1
42 | 37 | 38 | 5280 | 541 | 1
43 | 38 | 50 | 5280 | 542 | 1
44 | 38 | 44 | 5280 | 543 | 1
45 | 38 | 39 | 5280 | 544 | 1
46 | 39 | 51 | 5280 | 545 | 1
47 | 39 | 45 | 5280 | 546 | 1
48 | 39 | 40 | 5280 | 547 | 1
49 | 40 | 52 | 5280 | 548 | 1
50 | 40 | 46 | 5280 | 549 | 1
51 | 53 | 54 | 5280 | 550 | 1
52 | 54 | 59 | 5280 | 551 | 1
53 | 54 | 64 | 5280 | 552 | 1
54 | 54 | 55 | 5280 | 553 | 1
55 | 55 | 60 | 5280 | 554 | 1
56 | 55 | 65 | 5280 | 555 | 1
57 | 55 | 56 | 5280 | 556 | 1
58 | 56 | 61 | 5280 | 557 | 1
59 | 56 | 66 | 5280 | 558 | 1
60 | 56 | 57 | 5280 | 559 | 1
61 | 57 | 62 | 5280 | 560 | 1
62 | 57 | 67 | 5280 | 561 | 1
63 | 57 | 58 | 5280 | 562 | 1
64 | 58 | 68 | 5280 | 563 | 1
65 | 58 | 63 | 5280 | 564 | 1
66 | 69 | 70 | 5280 | 565 | 1
67 | 70 | 74 | 5280 | 566 | 1
68 | 70 | 78 | 5280 | 567 | 1
69 | 70 | 71 | 5280 | 568 | 1
70 | 71 | 75 | 5280 | 569 | 1
71 | 71 | 79 | 5280 | 570 | 1
72 | 71 | 72 | 5280 | 571 | 1
73 | 72 | 76 | 5280 | 572 | 1
74 | 72 | 80 | 5280 | 573 | 1
75 | 72 | 73 | 5280 | 574 | 1
76 | 73 | 77 | 5280 | 575 | 1
77 | 73 | 81 | 5280 | 576 | 1
78 | 82 | 83 | 5280 | 577 | 1
79 | 83 | 87 | 5280 | 578 | 1
80 | 83 | 91 | 5280 | 579 | 1
81 | 83 | 84 | 5280 | 580 | 1
82 | 84 | 88 | 5280 | 581 | 1
83 | 84 | 92 | 5280 | 582 | 1
84 | 84 | 85 | 5280 | 583 | 1
85 | 85 | 89 | 5280 | 584 | 1
86 | 85 | 93 | 5280 | 585 | 1
87 | 85 | 86 | 5280 | 586 | 1
88 | 86 | 90 | 5280 | 587 | 1
89 | 86 | 94 | 5280 | 588 | 1
90 | 95 | 96 | 5280 | 589 | 1
91 | 96 | 100 | 5280 | 590 | 1
92 | 96 | 104 | 5280 | 591 | 1
93 | 96 | 97 | 5280 | 592 | 1
94 | 97 | 101 | 5280 | 593 | 1
95 | 97 | 105 | 5280 | 594 | 1
96 | 97 | 98 | 5280 | 595 | 1
97 | 98 | 102 | 5280 | 596 | 1
98 | 98 | 106 | 5280 | 597 | 1
99 | 98 | 99 | 5280 | 598 | 1
100 | 99 | 103 | 5280 | 599 | 1
101 | 99 | 107 | 5280 | 600 | 1
102 | 108 | 109 | 5280 | 601 | 1
103 | 109 | 115 | 5280 | 602 | 1
104 | 109 | 121 | 5280 | 603 | 1
105 | 109 | 110 | 5280 | 604 | 1
106 | 110 | 116 | 5280 | 605 | 1
107 | 110 | 122 | 5280 | 606 | 1
108 | 110 | 111 | 5280 | 607 | 1
109 | 111 | 117 | 5280 | 608 | 1
110 | 111 | 123 | 5280 | 609 | 1
111 | 111 | 112 | 5280 | 610 | 1
112 | 112 | 124 | 5280 | 611 | 1
113 | 112 | 118 | 5280 | 612 | 1
114 | 112 | 113 | 5280 | 613 | 1
115 | 113 | 125 | 5280 | 614 | 1
116 | 113 | 119 | 5280 | 615 | 1
117 | 113 | 114 | 5280 | 616 | 1
118 | 114 | 126 | 5280 | 617 | 1
119 | 114 | 120 | 5280 | 618 | 1
120 | 127 | 128 | 5280 | 619 | 1
121 | 128 | 134 | 5280 | 620 | 1
122 | 128 | 140 | 5280 | 621 | 1
123 | 128 | 129 | 5280 | 622 | 1
124 | 129 | 135 | 5280 | 623 | 1
125 | 129 | 141 | 5280 | 624 | 1
126 | 129 | 130 | 5280 | 625 | 1
127 | 130 | 136 | 5280 | 626 | 1
128 | 130 | 142 | 5280 | 627 | 1
129 | 130 | 131 | 5280 | 628 | 1
130 | 131 | 143 | 5280 | 629 | 1
131 | 131 | 137 | 5280 | 630 | 1
132 | 131 | 132 | 5280 | 631 | 1
133 | 132 | 144 | 5280 | 632 | 1
134 | 132 | 138 | 5280 | 633 | 1
135 | 132 | 133 | 5280 | 634 | 1
136 | 133 | 145 | 5280 | 635 | 1
137 | 133 | 139 | 5280 | 636 | 1
138 | 146 | 147 | 5280 | 637 | 1
139 | 147 | 153 | 5280 | 638 | 1
140 | 147 | 159 | 5280 | 639 | 1
141 | 147 | 148 | 5280 | 640 | 1
142 | 148 | 154 | 5280 | 641 | 1
143 | 148 | 160 | 5280 | 642 | 1
144 | 148 | 149 | 5280 | 643 | 1
145 | 149 | 155 | 5280 | 644 | 1
146 | 149 | 161 | 5280 | 645 | 1
147 | 149 | 150 | 5280 | 646 | 1
148 | 150 | 162 | 5280 | 647 | 1
149 | 150 | 156 | 5280 | 648 | 1
150 | 150 | 151 | 5280 | 649 | 1
151 | 151 | 163 | 5280 | 650 | 1
152 | 151 | 157 | 5280 | 651 | 1
153 | 151 | 152 | 5280 | 652 | 1
154 | 152 | 164 | 5280 | 653 | 1
155 | 152 | 158 | 5280 | 654 | 1
156 | 165 | 166 | 5280 | 655 | 1
157 | 166 | 172 | 5280 | 656 | 1
158 | 166 | 178 | 5280 | 657 | 1
159 | 166 | 167 | 5280 | 658 | 1
160 | 167 | 173 | 5280 | 659 | 1
161 | 167 | 179 | 5280 | 660 | 1
162 | 167 | 168 | 5280 | 661 | 1
163 | 168 | 174 | 5280 | 662 | 1
164 | 168 | 180 | 5280 | 663 | 1
165 | 168 | 169 | 5280 | 664 | 1
166 | 169 | 181 | 5280 | 665 | 1
167 | 169 | 175 | 5280 | 666 | 1
168 | 169 | 170 | 5280 | 667 | 1
169 | 170 | 182 | 5280 | 668 | 1
170 | 170 | 176 | 5280 | 669 | 1
171 | 170 | 171 | 5280 | 670 | 1
172 | 171 | 183 | 5280 | 671 | 1
173 | 171 | 177 | 5280 | 672 | 1
174 | 184 | 185 | 5280 | 673 | 1
175 | 185 | 189 | 5280 | 674 | 1
176 | 185 | 193 | 5280 | 675 | 1
177 | 185 | 186 | 5280 | 676 | 1
178 | 186 | 190 | 5280 | 677 | 1
179 | 186 | 194 | 5280 | 678 | 1
180 | 186 | 187 | 5280 | 679 | 1
181 | 187 | 191 | 5280 | 680 | 1
182 | 187 | 195 | 5280 | 681 | 1
183 | 187 | 188 | 5280 | 682 | 1
184 | 188 | 192 | 5280 | 683 | 1
185 | 188 | 196 | 5280 | 684 | 1
186 | 197 | 198 | 5280 | 685 | 1
187 | 198 | 202 | 5280 | 686 | 1
188 | 198 | 206 | 5280 | 687 | 1
189 | 198 | 199 | 5280 | 688 | 1
190 | 199 | 203 | 5280 | 689 | 1
191 | 199 | 207 | 5280 | 690 | 1
192 | 199 | 200 | 5280 | 691 | 1
193 | 200 | 204 | 5280 | 692 | 1
194 | 200 | 208 | 5280 | 693 | 1
195 | 200 | 201 | 5280 | 694 | 1
196 | 201 | 205 | 5280 | 695 | 1
197 | 201 | 209 | 5280 | 696 | 1
198 | 210 | 211 | 5280 | 697 | 1
199 | 211 | 214 | 5280 | 698 | 1
200 | 211 | 217 | 5280 | 699 | 1
201 | 211 | 212 | 5280 | 700 | 1
202 | 212 | 215 | 5280 | 701 | 1
203 | 212 | 218 | 5280 | 702 | 1
204 | 212 | 213 | 5280 | 703 | 1
205 | 213 | 216 | 5280 | 704 | 1
206 | 213 | 219 | 5280 | 705 | 1
207 | 220 | 221 | 5280 | 706 | 1
208 | 221 | 225 | 5280 | 707 | 1
209 | 221 | 229 | 5280 | 708 | 1
210 | 221 | 222 | 5280 | 709 | 1
211 | 222 | 226 | 5280 | 710 | 1
212 | 222 | 230 | 5280 | 711 | 1
213 | 222 | 223 | 5280 | 712 | 1
214 | 223 | 227 | 5280 | 713 | 1
215 | 223 | 231 | 5280 | 714 | 1
216 | 223 | 224 | 5280 | 715 | 1
217 | 224 | 228 | 5280 | 716 | 1
218 | 224 | 232 | 5280 | 717 | 1
219 | 233 | 234 | 5280 | 718 | 1
220 | 234 | 238 | 5280 | 719 | 1
221 | 234 | 242 | 5280 | 720 | 1
222 | 234 | 235 | 5280 | 721 | 1
223 | 235 | 239 | 5280 | 722 | 1
224 | 235 | 243 | 5280 | 723 | 1
225 | 235 | 236 | 5280 | 724 | 1
226 | 236 | 240 | 5280 | 725 | 1
227 | 236 | 244 | 5280 | 726 | 1
228 | 236 | 237 | 5280 | 727 | 1
229 | 237 | 241 | 5280 | 728 | 1
230 | 237 | 245 | 5280 | 729 | 1
231 | 246 | 247 | 5280 | 730 | 1
232 | 247 | 253 | 5280 | 731 | 1
233 | 247 | 259 | 5280 | 732 | 1
234 | 247 | 248 | 5280 | 733 | 1
235 | 248 | 254 | 5280 | 734 | 1
236 | 248 | 260 | 5280 | 735 | 1
237 | 248 | 249 | 5280 | 736 | 1
238 | 249 | 255 | 5280 | 737 | 1
239 | 249 | 261 | 5280 | 738 | 1
240 | 249 | 250 | 5280 | 739 | 1
241 | 250 | 262 | 5280 | 740 | 1
242 | 250 | 256 | 5280 | 741 | 1
243 | 250 | 251 | 5280 | 742 | 1
244 | 251 | 263 | 5280 | 743 | 1
245 | 251 | 257 | 5280 | 744 | 1
246 | 251 | 252 | 5280 | 745 | 1
247 | 252 | 264 | 5280 | 746 | 1
248 | 252 | 258 | 5280 | 747 | 1
249 | 265 | 266 | 5280 | 748 | 1
250 | 266 | 270 | 5280 | 749 | 1
251 | 266 | 274 | 5280 | 750 | 1
252 | 266 | 267 | 5280 | 751 | 1
253 | 267 | 271 | 5280 | 752 | 1
254 | 267 | 275 | 5280 | 753 | 1
255 | 267 | 268 | 5280 | 754 | 1
256 | 268 | 272 | 5280 | 755 | 1
257 | 268 | 276 | 5280 | 756 | 1
258 | 268 | 269 | 5280 | 757 | 1
259 | 269 | 273 | 5280 | 758 | 1
260 | 269 | 277 | 5280 | 759 | 1
261 | 278 | 279 | 5280 | 760 | 1
262 | 279 | 283 | 5280 | 761 | 1
263 | 279 | 287 | 5280 | 762 | 1
264 | 279 | 280 | 5280 | 763 | 1
265 | 280 | 284 | 5280 | 764 | 1
266 | 280 | 288 | 5280 | 765 | 1
267 | 280 | 281 | 5280 | 766 | 1
268 | 281 | 285 | 5280 | 767 | 1
269 | 281 | 289 | 5280 | 768 | 1
270 | 281 | 282 | 5280 | 769 | 1
271 | 282 | 286 | 5280 | 770 | 1
272 | 282 | 290 | 5280 | 771 | 1
273 | 291 | 292 | 5280 | 772 | 1
274 | 292 | 296 | 5280 | 773 | 1
275 | 292 | 300 | 5280 | 774 | 1
276 | 292 | 293 | 5280 | 775 | 1
277 | 293 | 297 | 5280 | 776 | 1
278 | 293 | 301 | 5280 | 777 | 1
279 | 293 | 294 | 5280 | 778 | 1
280 | 294 | 298 | 5280 | 779 | 1
281 | 294 | 302 | 5280 | 780 | 1
282 | 294 | 295 | 5280 | 781 | 1
283 | 295 | 299 | 5280 | 782 | 1
284 | 295 | 303 | 5280 | 783 | 1
285 | 304 | 305 | 5280 | 784 | 1
286 | 305 | 310 | 5280 | 785 | 1
287 | 305 | 315 | 5280 | 786 | 1
288 | 305 | 306 | 5280 | 787 | 1
289 | 306 | 311 | 5280 | 788 | 1
290 | 306 | 316 | 5280 | 789 | 1
291 | 306 | 307 | 5280 | 790 | 1
292 | 307 | 312 | 5280 | 791 | 1
293 | 307 | 317 | 5280 | 792 | 1
294 | 307 | 308 | 5280 | 793 | 1
295 | 308 | 313 | 5280 | 794 | 1
296 | 308 | 318 | 5280 | 795 | 1
297 | 308 | 309 | 5280 | 796 | 1
298 | 309 | 319 | 5280 | 797 | 1
299 | 309 | 314 | 5280 | 798 | 1
300 | 320 | 321 | 5280 | 799 | 1
301 | 321 | 326 | 5280 | 800 | 1
302 | 321 | 331 | 5280 | 801 | 1
303 | 321 | 322 | 5280 | 802 | 1
304 | 322 | 327 | 5280 | 803 | 1
305 | 322 | 332 | 5280 | 804 | 1
306 | 322 | 323 | 5280 | 805 | 1
307 | 323 | 328 | 5280 | 806 | 1
308 | 323 | 333 | 5280 | 807 | 1
309 | 323 | 324 | 5280 | 808 | 1
310 | 324 | 329 | 5280 | 809 | 1
311 | 324 | 334 | 5280 | 810 | 1
312 | 324 | 325 | 5280 | 811 | 1
313 | 325 | 335 | 5280 | 812 | 1
314 | 325 | 330 | 5280 | 813 | 1
315 | 336 | 337 | 5280 | 814 | 1
316 | 337 | 342 | 5280 | 815 | 1
317 | 337 | 347 | 5280 | 816 | 1
318 | 337 | 338 | 5280 | 817 | 1
319 | 338 | 343 | 5280 | 818 | 1
320 | 338 | 348 | 5280 | 819 | 1
321 | 338 | 339 | 5280 | 820 | 1
322 | 339 | 344 | 5280 | 821 | 1
323 | 339 | 349 | 5280 | 822 | 1
324 | 339 | 340 | 5280 | 823 | 1
325 | 340 | 345 | 5280 | 824 | 1
326 | 340 | 350 | 5280 | 825 | 1
327 | 340 | 341 | 5280 | 826 | 1
328 | 341 | 351 | 5280 | 827 | 1
329 | 341 | 346 | 5280 | 828 | 1
330 | 352 | 353 | 5280 | 829 | 1
331 | 353 | 358 | 5280 | 830 | 1
332 | 353 | 363 | 5280 | 831 | 1
333 | 353 | 354 | 5280 | 832 | 1
334 | 354 | 359 | 5280 | 833 | 1
335 | 354 | 364 | 5280 | 834 | 1
336 | 354 | 355 | 5280 | 835 | 1
337 | 355 | 360 | 5280 | 836 | 1
338 | 355 | 365 | 5280 | 837 | 1
339 | 355 | 356 | 5280 | 838 | 1
340 | 356 | 361 | 5280 | 839 | 1
341 | 356 | 366 | 5280 | 840 | 1
342 | 356 | 357 | 5280 | 841 | 1
343 | 357 | 367 | 5280 | 842 | 1
344 | 357 | 362 | 5280 | 843 | 1
345 | 368 | 369 | 5280 | 844 | 1
346 | 369 | 374 | 5280 | 845 | 1
347 | 369 | 379 | 5280 | 846 | 1
348 | 369 | 370 | 5280 | 847 | 1
349 | 370 | 375 | 5280 | 848 | 1
350 | 370 | 380 | 5280 | 849 | 1
351 | 370 | 371 | 5280 | 850 | 1
352 | 371 | 376 | 5280 | 851 | 1
353 | 371 | 381 | 5280 | 852 | 1
354 | 371 | 372 | 5280 | 853 | 1
355 | 372 | 377 | 5280 | 854 | 1
356 | 372 | 382 | 5280 | 855 | 1
357 | 372 | 373 | 5280 | 856 | 1
358 | 373 | 383 | 5280 | 857 | 1
359 | 373 | 378 | 5280 | 858 | 1
360 | 384 | 385 | 5280 | 859 | 1
361 | 385 | 390 | 5280 | 860 | 1
362 | 385 | 395 | 5280 | 861 | 1
363 | 385 | 386 | 5280 | 862 | 1
364 | 386 | 391 | 5280 | 863 | 1
365 | 386 | 396 | 5280 | 864 | 1
366 | 386 | 387 | 5280 | 865 | 1
367 | 387 | 392 | 5280 | 866 | 1
368 | 387 | 397 | 5280 | 867 | 1
369 | 387 | 388 | 5280 | 868 | 1
370 | 388 | 393 | 5280 | 869 | 1
371 | 388 | 398 | 5280 | 870 | 1
372 | 388 | 389 | 5280 | 871 | 1
373 | 389 | 399 | 5280 | 872 | 1
374 | 389 | 394 | 5280 | 873 | 1
375 | 400 | 401 | 5280 | 874 | 1
376 | 401 | 407 | 5280 | 875 | 1
377 | 401 | 413 | 5280 | 876 | 1
378 | 401 | 402 | 5280 | 877 | 1
379 | 402 | 408 | 5280 | 878 | 1
380 | 402 | 414 | 5280 | 879 | 1
381 | 402 | 403 | 5280 | 880 | 1
382 | 403 | 409 | 5280 | 881 | 1
383 | 403 | 415 | 5280 | 882 | 1
384 | 403 | 404 | 5280 | 883 | 1
385 | 404 | 416 | 5280 | 884 | 1
386 | 404 | 410 | 5280 | 885 | 1
387 | 404 | 405 | 5280 | 886 | 1
388 | 405 | 417 | 5280 | 887 | 1
389 | 405 | 411 | 5280 | 888 | 1
390 | 405 | 406 | 5280 | 889 | 1
391 | 406 | 418 | 5280 | 890 | 1
392 | 406 | 412 | 5280 | 891 | 1
393 | 419 | 420 | 5280 | 892 | 1
394 | 420 | 426 | 5280 | 893 | 1
395 | 420 | 432 | 5280 | 894 | 1
396 | 420 | 421 | 5280 | 895 | 1
397 | 421 | 427 | 5280 | 896 | 1
398 | 421 | 433 | 5280 | 897 | 1
399 | 421 | 422 | 5280 | 898 | 1
400 | 422 | 428 | 5280 | 899 | 1
401 | 422 | 434 | 5280 | 900 | 1
402 | 422 | 423 | 5280 | 901 | 1
403 | 423 | 435 | 5280 | 902 | 1
404 | 423 | 429 | 5280 | 903 | 1
405 | 423 | 424 | 5280 | 904 | 1
406 | 424 | 436 | 5280 | 905 | 1
407 | 424 | 430 | 5280 | 906 | 1
408 | 424 | 425 | 5280 | 907 | 1
409 | 425 | 437 | 5280 | 908 | 1
410 | 425 | 431 | 5280 | 909 | 1
411 | 438 | 439 | 5280 | 910 | 1
412 | 439 | 445 | 5280 | 911 | 1
413 | 439 | 451 | 5280 | 912 | 1
414 | 439 | 440 | 5280 | 913 | 1
415 | 440 | 446 | 5280 | 914 | 1
416 | 440 | 452 | 5280 | 915 | 1
417 | 440 | 441 | 5280 | 916 | 1
418 | 441 | 447 | 5280 | 917 | 1
419 | 441 | 453 | 5280 | 918 | 1
420 | 441 | 442 | 5280 | 919 | 1
421 | 442 | 454 | 5280 | 920 | 1
422 | 442 | 448 | 5280 | 921 | 1
423 | 442 | 443 | 5280 | 922 | 1
424 | 443 | 455 | 5280 | 923 | 1
425 | 443 | 449 | 5280 | 924 | 1
426 | 443 | 444 | 5280 | 925 | 1
427 | 444 | 456 | 5280 | 926 | 1
428 | 444 | 450 | 5280 | 927 | 1
429 | 457 | 458 | 5280 | 928 | 1
430 | 458 | 464 | 5280 | 929 | 1
431 | 458 | 470 | 5280 | 930 | 1
432 | 458 | 459 | 5280 | 931 | 1
433 | 459 | 465 | 5280 | 932 | 1
434 | 459 | 471 | 5280 | 933 | 1
435 | 459 | 460 | 5280 | 934 | 1
436 | 460 | 466 | 5280 | 935 | 1
437 | 460 | 472 | 5280 | 936 | 1
438 | 460 | 461 | 5280 | 937 | 1
439 | 461 | 473 | 5280 | 938 | 1
440 | 461 | 467 | 5280 | 939 | 1
441 | 461 | 462 | 5280 | 940 | 1
442 | 462 | 474 | 5280 | 941 | 1
443 | 462 | 468 | 5280 | 942 | 1
444 | 462 | 463 | 5280 | 943 | 1
445 | 463 | 475 | 5280 | 944 | 1
446 | 463 | 469 | 5280 | 945 | 1
447 | 476 | 477 | 5280 | 946 | 1
448 | 477 | 483 | 5280 | 947 | 1
449 | 477 | 489 | 5280 | 948 | 1
450 | 477 | 478 | 5280 | 949 | 1
451 | 478 | 484 | 5280 | 950 | 1
452 | 478 | 490 | 5280 | 951 | 1
453 | 478 | 479 | 5280 | 952 | 1
454 | 479 | 485 | 5280 | 953 | 1
455 | 479 | 491 | 5280 | 954 | 1
456 | 479 | 480 | 5280 | 955 | 1
457 | 480 | 492 | 5280 | 956 | 1
458 | 480 | 486 | 5280 | 957 | 1
459 | 480 | 481 | 5280 | 958 | 1
460 | 481 | 493 | 5280 | 959 | 1
461 | 481 | 487 | 5280 | 960 | 1
462 | 481 | 482 | 5280 | 961 | 1
463 | 482 | 494 | 5280 | 962 | 1
464 | 482 | 488 | 5280 | 963 | 1
465 | 495 | 496 | 5280 | 964 | 1
466 | 496 | 502 | 5280 | 965 | 1
467 | 496 | 508 | 5280 | 966 | 1
468 | 496 | 497 | 5280 | 967 | 1
469 | 497 | 503 | 5280 | 968 | 1
470 | 497 | 509 | 5280 | 969 | 1
471 | 497 | 498 | 5280 | 970 | 1
472 | 498 | 504 | 5280 | 971 | 1
473 | 498 | 510 | 5280 | 972 | 1
474 | 498 | 499 | 5280 | 973 | 1
475 | 499 | 511 | 5280 | 974 | 1
476 | 499 | 505 | 5280 | 975 | 1
477 | 499 | 500 | 5280 | 976 | 1
478 | 500 | 512 | 5280 | 977 | 1
479 | 500 | 506 | 5280 | 978 | 1
480 | 500 | 501 | 5280 | 979 | 1
481 | 501 | 513 | 5280 | 980 | 1
482 | 501 | 507 | 5280 | 981 | 1
483 | 514 | 515 | 5280 | 982 | 1
484 | 515 | 521 | 5280 | 983 | 1
485 | 515 | 527 | 5280 | 984 | 1
486 | 515 | 516 | 5280 | 985 | 1
487 | 516 | 522 | 5280 | 986 | 1
488 | 516 | 528 | 5280 | 987 | 1
489 | 516 | 517 | 5280 | 988 | 1
490 | 517 | 523 | 5280 | 989 | 1
491 | 517 | 529 | 5280 | 990 | 1
492 | 517 | 518 | 5280 | 991 | 1
493 | 518 | 530 | 5280 | 992 | 1
494 | 518 | 524 | 5280 | 993 | 1
495 | 518 | 519 | 5280 | 994 | 1
496 | 519 | 531 | 5280 | 995 | 1
497 | 519 | 525 | 5280 | 996 | 1
498 | 519 | 520 | 5280 | 997 | 1
499 | 520 | 532 | 5280 | 998 | 1
500 | 520 | 526 | 5280 | 999 | 1
501 | 533 | 534 | 5280 | 1000 | 1
502 | 534 | 540 | 5280 | 1001 | 1
503 | 534 | 546 | 5280 | 1002 | 1
504 | 534 | 535 | 5280 | 1003 | 1
505 | 535 | 541 | 5280 | 1004 | 1
506 | 535 | 547 | 5280 | 1005 | 1
507 | 535 | 536 | 5280 | 1006 | 1
508 | 536 | 542 | 5280 | 1007 | 1
509 | 536 | 548 | 5280 | 1008 | 1
510 | 536 | 537 | 5280 | 1009 | 1
511 | 537 | 549 | 5280 | 1010 | 1
512 | 537 | 543 | 5280 | 1011 | 1
513 | 537 | 538 | 5280 | 1012 | 1
514 | 538 | 550 | 5280 | 1013 | 1
515 | 538 | 544 | 5280 | 1014 | 1
516 | 538 | 539 | 5280 | 1015 | 1
517 | 539 | 551 | 5280 | 1016 | 1
518 | 539 | 545 | 5280 | 1017 | 1
519 | 552 | 557 | 5280 | 1018 | 1
520 | 552 | 561 | 5280 | 1019 | 1
521 | 552 | 553 | 5280 | 1020 | 1
522 | 553 | 558 | 5280 | 1021 | 1
523 | 553 | 562 | 5280 | 1022 | 1
524 | 553 | 554 | 5280 | 1023 | 1
525 | 554 | 559 | 5280 | 1024 | 1
526 | 554 | 563 | 5280 | 1025 | 1
527 | 554 | 555 | 5280 | 1026 | 1
528 | 555 | 560 | 5280 | 1027 | 1
529 | 555 | 564 | 5280 | 1028 | 1
530 | 555 | 556 | 5280 | 1029 | 1
531 | 565 | 566 | 5280 | 1030 | 1
532 | 566 | 570 | 5280 | 1031 | 1
533 | 566 | 574 | 5280 | 1032 | 1
534 | 566 | 567 | 5280 | 1033 | 1
535 | 567 | 571 | 5280 | 1034 | 1
536 | 567 | 575 | 5280 | 1035 | 1
537 | 567 | 568 | 5280 | 1036 | 1
538 | 568 | 572 | 5280 | 1037 | 1
539 | 568 | 576 | 5280 | 1038 | 1
540 | 568 | 569 | 5280 | 1039 | 1
541 | 569 | 573 | 5280 | 1040 | 1
542 | 569 | 577 | 5280 | 1041 | 1
543 | 578 | 579 | 5280 | 1042 | 1
544 | 579 | 583 | 5280 | 1043 | 1
545 | 579 | 587 | 5280 | 1044 | 1
546 | 579 | 580 | 5280 | 1045 | 1
547 | 580 | 584 | 5280 | 1046 | 1
548 | 580 | 588 | 5280 | 1047 | 1
549 | 580 | 581 | 5280 | 1048 | 1
550 | 581 | 585 | 5280 | 1049 | 1
551 | 581 | 589 | 5280 | 1050 | 1
552 | 581 | 582 | 5280 | 1051 | 1
553 | 582 | 586 | 5280 | 1052 | 1
554 | 582 | 590 | 5280 | 1053 | 1
555 | 591 | 592 | 5280 | 1054 | 1
556 | 592 | 598 | 5280 | 1055 | 1
557 | 592 | 604 | 5280 | 1056 | 1
558 | 592 | 593 | 5280 | 1057 | 1
559 | 593 | 599 | 5280 | 1058 | 1
560 | 593 | 605 | 5280 | 1059 | 1
561 | 593 | 594 | 5280 | 1060 | 1
562 | 594 | 600 | 5280 | 1061 | 1
563 | 594 | 606 | 5280 | 1062 | 1
564 | 594 | 595 | 5280 | 1063 | 1
565 | 595 | 607 | 5280 | 1064 | 1
566 | 595 | 601 | 5280 | 1065 | 1
567 | 595 | 596 | 5280 | 1066 | 1
568 | 596 | 608 | 5280 | 1067 | 1
569 | 596 | 602 | 5280 | 1068 | 1
570 | 596 | 597 | 5280 | 1069 | 1
571 | 597 | 609 | 5280 | 1070 | 1
572 | 597 | 603 | 5280 | 1071 | 1
573 | 610 | 611 | 5280 | 1072 | 1
574 | 611 | 617 | 5280 | 1073 | 1
575 | 611 | 623 | 5280 | 1074 | 1
576 | 611 | 612 | 5280 | 1075 | 1
577 | 612 | 618 | 5280 | 1076 | 1
578 | 612 | 624 | 5280 | 1077 | 1
579 | 612 | 613 | 5280 | 1078 | 1
580 | 613 | 619 | 5280 | 1079 | 1
581 | 613 | 625 | 5280 | 1080 | 1
582 | 613 | 614 | 5280 | 1081 | 1
583 | 614 | 626 | 5280 | 1082 | 1
584 | 614 | 620 | 5280 | 1083 | 1
585 | 614 | 615 | 5280 | 1084 | 1
586 | 615 | 627 | 5280 | 1085 | 1
587 | 615 | 621 | 5280 | 1086 | 1
588 | 615 | 616 | 5280 | 1087 | 1
589 | 616 | 628 | 5280 | 1088 | 1
590 | 616 | 622 | 5280 | 1089 | 1
591 | 629 | 630 | 5280 | 1090 | 1
592 | 630 | 636 | 5280 | 1091 | 1
593 | 630 | 642 | 5280 | 1092 | 1
594 | 630 | 631 | 5280 | 1093 | 1
595 | 631 | 637 | 5280 | 1094 | 1
596 | 631 | 643 | 5280 | 1095 | 1
597 | 631 | 632 | 5280 | 1096 | 1
598 | 632 | 638 | 5280 | 1097 | 1
599 | 632 | 644 | 5280 | 1098 | 1
600 | 632 | 633 | 5280 | 1099 | 1
601 | 633 | 645 | 5280 | 1100 | 1
602 | 633 | 639 | 5280 | 1101 | 1
603 | 633 | 634 | 5280 | 1102 | 1
604 | 634 | 646 | 5280 | 1103 | 1
605 | 634 | 640 | 5280 | 1104 | 1
606 | 634 | 635 | 5280 | 1105 | 1
607 | 635 | 647 | 5280 | 1106 | 1
608 | 635 | 641 | 5280 | 1107 | 1
609 | 648 | 649 | 5280 | 1108 | 1
610 | 649 | 654 | 5280 | 1109 | 1
611 | 649 | 659 | 5280 | 1110 | 1
612 | 649 | 650 | 5280 | 1111 | 1
613 | 650 | 655 | 5280 | 1112 | 1
614 | 650 | 660 | 5280 | 1113 | 1
615 | 650 | 651 | 5280 | 1114 | 1
616 | 651 | 656 | 5280 | 1115 | 1
617 | 651 | 661 | 5280 | 1116 | 1
618 | 651 | 652 | 5280 | 1117 | 1
619 | 652 | 657 | 5280 | 1118 | 1
620 | 652 | 662 | 5280 | 1119 | 1
621 | 652 | 653 | 5280 | 1120 | 1
622 | 653 | 663 | 5280 | 1121 | 1
623 | 653 | 658 | 5280 | 1122 | 1
624 | 664 | 665 | 5280 | 1123 | 1
625 | 665 | 670 | 5280 | 1124 | 1
626 | 665 | 675 | 5280 | 1125 | 1
627 | 665 | 666 | 5280 | 1126 | 1
628 | 666 | 671 | 5280 | 1127 | 1
629 | 666 | 676 | 5280 | 1128 | 1
630 | 666 | 667 | 5280 | 1129 | 1
631 | 667 | 672 | 5280 | 1130 | 1
632 | 667 | 677 | 5280 | 1131 | 1
633 | 667 | 668 | 5280 | 1132 | 1
634 | 668 | 673 | 5280 | 1133 | 1
635 | 668 | 678 | 5280 | 1134 | 1
636 | 668 | 669 | 5280 | 1135 | 1
637 | 669 | 679 | 5280 | 1136 | 1
638 | 669 | 674 | 5280 | 1137 | 1
639 | 680 | 681 | 5280 | 1138 | 1
640 | 681 | 687 | 5280 | 1139 | 1
641 | 681 | 693 | 5280 | 1140 | 1
642 | 681 | 682 | 5280 | 1141 | 1
643 | 682 | 688 | 5280 | 1142 | 1
644 | 682 | 694 | 5280 | 1143 | 1
645 | 682 | 683 | 5280 | 1144 | 1
646 | 683 | 689 | 5280 | 1145 | 1
647 | 683 | 695 | 5280 | 1146 | 1
648 | 683 | 684 | 5280 | 1147 | 1
649 | 684 | 696 | 5280 | 1148 | 1
650 | 684 | 690 | 5280 | 1149 | 1
651 | 684 | 685 | 5280 | 1150 | 1
652 | 685 | 697 | 5280 | 1151 | 1
653 | 685 | 691 | 5280 | 1152 | 1
654 | 685 | 686 | 5280 | 1153 | 1
655 | 686 | 698 | 5280 | 1154 | 1
656 | 686 | 692 | 5280 | 1155 | 1
657 | 699 | 700 | 5280 | 1156 | 1
658 | 700 | 706 | 5280 | 1157 | 1
659 | 700 | 712 | 5280 | 1158 | 1
660 | 700 | 701 | 5280 | 1159 | 1
661 | 701 | 707 | 5280 | 1160 | 1
662 | 701 | 713 | 5280 | 1161 | 1
663 | 701 | 702 | 5280 | 1162 | 1
664 | 702 | 708 | 5280 | 1163 | 1
665 | 702 | 714 | 5280 | 1164 | 1
666 | 702 | 703 | 5280 | 1165 | 1
667 | 703 | 715 | 5280 | 1166 | 1
668 | 703 | 709 | 5280 | 1167 | 1
669 | 703 | 704 | 5280 | 1168 | 1
670 | 704 | 716 | 5280 | 1169 | 1
671 | 704 | 710 | 5280 | 1170 | 1
672 | 704 | 705 | 5280 | 1171 | 1
673 | 705 | 717 | 5280 | 1172 | 1
674 | 705 | 711 | 5280 | 1173 | 1
675 | 718 | 719 | 5280 | 1174 | 1
676 | 719 | 723 | 5280 | 1175 | 1
677 | 719 | 727 | 5280 | 1176 | 1
678 | 719 | 720 | 5280 | 1177 | 1
679 | 720 | 724 | 5280 | 1178 | 1
680 | 720 | 728 | 5280 | 1179 | 1
681 | 720 | 721 | 5280 | 1180 | 1
682 | 721 | 725 | 5280 | 1181 | 1
683 | 721 | 729 | 5280 | 1182 | 1
684 | 721 | 722 | 5280 | 1183 | 1
685 | 722 | 726 | 5280 | 1184 | 1
686 | 722 | 730 | 5280 | 1185 | 1

## Transformers
TrfNo | TrfName | FromNode | ToNode | kVA | FNodekV | FromType | TNodekV | ToType | R% | X% | Status | kVAtype | kVA1 | kVA2 | kVA3 | r1% | x1% | r2% | x2% | r3% | x3% | Ng
101 | TRF101 | 2 | 34 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | TRF102 | 3 | 53 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | TRF103 | 4 | 69 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | TRF104 | 5 | 82 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | TRF105 | 6 | 95 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | TRF106 | 7 | 108 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | TRF107 | 7 | 127 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | TRF108 | 8 | 146 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | TRF109 | 8 | 165 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | TRF110 | 9 | 184 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | TRF111 | 10 | 197 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | TRF112 | 11 | 210 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | TRF113 | 12 | 220 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | TRF114 | 13 | 233 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | TRF115 | 14 | 246 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | TRF116 | 15 | 265 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | TRF117 | 16 | 278 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | TRF118 | 17 | 291 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | TRF119 | 18 | 304 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | TRF120 | 19 | 320 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | TRF121 | 20 | 336 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | TRF122 | 21 | 352 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | TRF123 | 22 | 368 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | TRF124 | 23 | 384 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | TRF125 | 24 | 400 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | TRF126 | 24 | 419 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | TRF127 | 24 | 438 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | TRF128 | 24 | 457 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | TRF129 | 25 | 476 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | TRF130 | 25 | 495 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | TRF131 | 25 | 514 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | TRF132 | 25 | 533 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | TRF133 | 26 | 552 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | TRF134 | 27 | 565 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | TRF135 | 28 | 578 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | TRF136 | 29 | 591 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | TRF137 | 30 | 610 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | TRF138 | 30 | 629 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | TRF139 | 31 | 648 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | TRF140 | 31 | 664 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | TRF141 | 32 | 680 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | TRF142 | 32 | 699 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | TRF143 | 33 | 718 | 1000 | 12.66 | 2 | 0.24 | 2 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Note on G1: Author: 0- Delta 1- WYE Ungrounded 2- WYE Grounded
Note on I1: Author: 0- Delta 1- WYE Ungrounded 2- WYE Grounded
Note on L1: Author: 0- Out of service 1- In service
Note on M1: Author: Flag 0- Trf as a single Three-phase unit Transformer. Flag 1- Three individual Transformers for each phase. Flag 3 - using User-Defined Transformer Library
Note on W1: Author: Neutral ground resistance

## Loads
Node | Load_Type | Load_Model | Ph-1_kW | Ph-1_kVAr | Ph-2_kW | Ph-2_kVAr | Ph-3_kW | Ph-3_kVAr | Ph1_flg | Ph2_flg | Ph3_flg | load_data | Status
41 | 1 | 0 | 6.4147 | 2.1382 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
42 | 1 | 0 | 6.2279 | 2.076 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
43 | 1 | 0 | 4.1947 | 1.3982 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
44 | 1 | 0 | 6.3622 | 2.1207 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
45 | 1 | 0 | 1.5589 | 0.51962 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
46 | 1 | 0 | 1.8034 | 0.60115 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
47 | 1 | 0 | 6.7702 | 2.2567 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
48 | 1 | 0 | 0.94137 | 0.31379 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
49 | 1 | 0 | 1.0193 | 0.33976 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
50 | 1 | 0 | 3.4884 | 1.1628 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
51 | 1 | 0 | 1.8653 | 0.62176 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
52 | 1 | 0 | 5.1272 | 1.7091 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
59 | 1 | 0 | 5.2396 | 1.7465 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
60 | 1 | 0 | 7.4071 | 2.469 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
61 | 1 | 0 | 1.4486 | 0.48286 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
62 | 1 | 0 | 1.4481 | 0.48269 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
63 | 1 | 0 | 1.1949 | 0.39829 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
64 | 1 | 0 | 9.8294 | 3.2765 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
65 | 1 | 0 | 4.394 | 1.4647 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
66 | 1 | 0 | 4.6715 | 1.5572 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
67 | 1 | 0 | 2.7966 | 0.93219 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
68 | 1 | 0 | 1.6513 | 0.55042 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
74 | 1 | 0 | 1.3774 | 0.45912 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
75 | 1 | 0 | 1.2733 | 0.42442 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
76 | 1 | 0 | 2.1227 | 0.70758 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
77 | 1 | 0 | 1.645 | 0.54834 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
78 | 1 | 0 | 1.1291 | 0.37637 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
79 | 1 | 0 | 2.1678 | 0.72261 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
80 | 1 | 0 | 2.2502 | 0.75006 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
81 | 1 | 0 | 1.5369 | 0.5123 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
87 | 1 | 0 | 1.0727 | 0.35756 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
88 | 1 | 0 | 2.6274 | 0.87581 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
89 | 1 | 0 | 0.65147 | 0.21716 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
90 | 1 | 0 | 1.2877 | 0.42924 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
91 | 1 | 0 | 1.364 | 0.45466 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
92 | 1 | 0 | 0.68642 | 0.22881 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
93 | 1 | 0 | 1.3792 | 0.45974 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
94 | 1 | 0 | 2.953 | 0.98434 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
100 | 1 | 0 | 1.3341 | 0.4447 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
101 | 1 | 0 | 5.1677 | 1.7226 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
102 | 1 | 0 | 3.1159 | 1.0386 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
103 | 1 | 0 | 0.68738 | 0.22913 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
104 | 1 | 0 | 2.4447 | 0.81488 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
105 | 1 | 0 | 2.2612 | 0.75372 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
106 | 1 | 0 | 2.7887 | 0.92956 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
107 | 1 | 0 | 4.4402 | 1.4801 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
115 | 1 | 0 | 2.3556 | 0.78522 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
116 | 1 | 0 | 0.92425 | 0.30808 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
117 | 1 | 0 | 2.5165 | 0.83882 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
118 | 1 | 0 | 2.438 | 0.81266 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
119 | 1 | 0 | 2.9533 | 0.98444 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
120 | 1 | 0 | 1.5118 | 0.50392 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
121 | 1 | 0 | 2.2035 | 0.73448 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
122 | 1 | 0 | 2.629 | 0.87633 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
123 | 1 | 0 | 1.3911 | 0.46369 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
124 | 1 | 0 | 2.2088 | 0.73628 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
125 | 1 | 0 | 1.9866 | 0.66219 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
126 | 1 | 0 | 1.7659 | 0.58862 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
134 | 1 | 0 | 2.1328 | 0.71094 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
135 | 1 | 0 | 1.3819 | 0.46064 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
136 | 1 | 0 | 3.0164 | 1.0055 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
137 | 1 | 0 | 2.179 | 0.72634 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
138 | 1 | 0 | 3.1971 | 1.0657 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
139 | 1 | 0 | 1.685 | 0.56167 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
140 | 1 | 0 | 2.6078 | 0.86927 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
141 | 1 | 0 | 2.6271 | 0.87572 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
142 | 1 | 0 | 1.6013 | 0.53376 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
143 | 1 | 0 | 1.6874 | 0.56248 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
144 | 1 | 0 | 2.0992 | 0.69972 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
145 | 1 | 0 | 1.5845 | 0.52816 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
153 | 1 | 0 | 1.6047 | 0.5349 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
154 | 1 | 0 | 1.502 | 0.50067 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
155 | 1 | 0 | 2.1311 | 0.71036 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
156 | 1 | 0 | 1.9909 | 0.66365 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
157 | 1 | 0 | 2.4154 | 0.80514 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
158 | 1 | 0 | 2.2648 | 0.75493 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
159 | 1 | 0 | 2.7053 | 0.90176 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
160 | 1 | 0 | 1.6863 | 0.56208 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
161 | 1 | 0 | 1.3314 | 0.44381 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
162 | 1 | 0 | 1.5796 | 0.52654 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
163 | 1 | 0 | 2.7346 | 0.91155 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
164 | 1 | 0 | 2.0007 | 0.66691 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
172 | 1 | 0 | 2.0447 | 0.68157 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
173 | 1 | 0 | 2.4185 | 0.80617 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
174 | 1 | 0 | 2.2095 | 0.7365 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
175 | 1 | 0 | 2.0605 | 0.68683 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
176 | 1 | 0 | 2.1267 | 0.70889 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
177 | 1 | 0 | 2.1631 | 0.72105 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
178 | 1 | 0 | 2.3852 | 0.79507 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
179 | 1 | 0 | 2.0714 | 0.69048 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
180 | 1 | 0 | 2.2221 | 0.74071 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
181 | 1 | 0 | 1.3239 | 0.4413 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
182 | 1 | 0 | 2.2505 | 0.75016 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
183 | 1 | 0 | 2.0567 | 0.68558 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
189 | 1 | 0 | 1.7957 | 0.59858 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
190 | 1 | 0 | 2.1224 | 0.70746 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
191 | 1 | 0 | 1.5112 | 0.50372 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
192 | 1 | 0 | 2.1052 | 0.70172 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
193 | 1 | 0 | 2.9294 | 0.97646 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
194 | 1 | 0 | 2.5037 | 0.83458 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
195 | 1 | 0 | 2.1462 | 0.71539 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
196 | 1 | 0 | 5.4909 | 1.8303 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
202 | 1 | 0 | 1.8989 | 0.63296 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
203 | 1 | 0 | 2.0611 | 0.68703 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
204 | 1 | 0 | 2.121 | 0.70701 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
205 | 1 | 0 | 2.1328 | 0.71094 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
206 | 1 | 0 | 2.1869 | 0.72898 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
207 | 1 | 0 | 5.086 | 1.6953 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
208 | 1 | 0 | 0.91218 | 0.30406 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
209 | 1 | 0 | 2.3101 | 0.77003 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
214 | 1 | 0 | 2.4441 | 0.81471 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
215 | 1 | 0 | 1.3521 | 0.45071 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
216 | 1 | 0 | 1.0994 | 0.36646 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
217 | 1 | 0 | 1.0751 | 0.35837 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
218 | 1 | 0 | 3.3757 | 1.1252 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
219 | 1 | 0 | 2.4868 | 0.82893 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
225 | 1 | 0 | 1.6398 | 0.54661 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
226 | 1 | 0 | 2.4611 | 0.82037 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
227 | 1 | 0 | 2.6749 | 0.89163 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
228 | 1 | 0 | 2.1733 | 0.72444 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
229 | 1 | 0 | 2.0871 | 0.6957 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
230 | 1 | 0 | 2.3617 | 0.78725 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
231 | 1 | 0 | 2.2117 | 0.73723 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
232 | 1 | 0 | 1.6295 | 0.54316 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
238 | 1 | 0 | 3.3971 | 1.1324 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
239 | 1 | 0 | 2.6847 | 0.8949 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
240 | 1 | 0 | 1.4654 | 0.48847 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
241 | 1 | 0 | 2.5448 | 0.84827 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
242 | 1 | 0 | 2.2409 | 0.74696 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
243 | 1 | 0 | 1.5565 | 0.51884 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
244 | 1 | 0 | 2.221 | 0.74033 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
245 | 1 | 0 | 2.0669 | 0.68895 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
253 | 1 | 0 | 0.87232 | 0.29077 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
254 | 1 | 0 | 0.698 | 0.23267 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
255 | 1 | 0 | 0.73297 | 0.24432 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
256 | 1 | 0 | 0.66898 | 0.22299 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
257 | 1 | 0 | 0.68323 | 0.22774 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
258 | 1 | 0 | 4.353 | 1.451 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
259 | 1 | 0 | 2.9771 | 0.99237 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
260 | 1 | 0 | 3.4472 | 1.1491 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
261 | 1 | 0 | 1.9922 | 0.66406 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
262 | 1 | 0 | 1.938 | 0.64598 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
263 | 1 | 0 | 2.1333 | 0.71111 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
264 | 1 | 0 | 2.7249 | 0.90829 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
270 | 1 | 0 | 3.1509 | 1.0503 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
271 | 1 | 0 | 3.0861 | 1.0287 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
272 | 1 | 0 | 2.4591 | 0.81969 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
273 | 1 | 0 | 2.3426 | 0.78087 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
274 | 1 | 0 | 1.6498 | 0.54993 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
275 | 1 | 0 | 1.6734 | 0.55779 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
276 | 1 | 0 | 2.2419 | 0.74729 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
277 | 1 | 0 | 3.2614 | 1.0871 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
283 | 1 | 0 | 2.9796 | 0.99322 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
284 | 1 | 0 | 1.7288 | 0.57628 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
285 | 1 | 0 | 1.1952 | 0.39842 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
286 | 1 | 0 | 1.1475 | 0.3825 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
287 | 1 | 0 | 2.7875 | 0.92917 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
288 | 1 | 0 | 2.138 | 0.71268 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
289 | 1 | 0 | 3.8065 | 1.2688 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
290 | 1 | 0 | 2.3026 | 0.76754 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
296 | 1 | 0 | 2.5833 | 0.8611 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
297 | 1 | 0 | 2.0843 | 0.69477 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
298 | 1 | 0 | 1.6604 | 0.55347 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
299 | 1 | 0 | 1.6003 | 0.53345 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
300 | 1 | 0 | 0.8872 | 0.29573 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
301 | 1 | 0 | 3.9812 | 1.3271 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
302 | 1 | 0 | 2.9123 | 0.97078 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
303 | 1 | 0 | 1.8833 | 0.62778 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
310 | 1 | 0 | 2.2228 | 0.74093 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
311 | 1 | 0 | 1.9422 | 0.6474 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
312 | 1 | 0 | 1.4254 | 0.47514 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
313 | 1 | 0 | 2.2949 | 0.76497 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
314 | 1 | 0 | 2.5 | 0.83332 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
315 | 1 | 0 | 0.58975 | 0.19658 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
316 | 1 | 0 | 1.2425 | 0.41417 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
317 | 1 | 0 | 1.3233 | 0.44108 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
318 | 1 | 0 | 2.5861 | 0.86204 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
319 | 1 | 0 | 1.5869 | 0.52896 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
326 | 1 | 0 | 1.3203 | 0.44011 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
327 | 1 | 0 | 0.58373 | 0.19458 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
328 | 1 | 0 | 0.78077 | 0.26026 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
329 | 1 | 0 | 1.3386 | 0.44619 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
330 | 1 | 0 | 8.9945 | 2.9982 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
331 | 1 | 0 | 1.3372 | 0.44572 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
332 | 1 | 0 | 2.6393 | 0.87978 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
333 | 1 | 0 | 1.5842 | 0.52806 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
334 | 1 | 0 | 2.306 | 0.76866 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
335 | 1 | 0 | 2.2333 | 0.74443 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
342 | 1 | 0 | 1.7061 | 0.56871 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
343 | 1 | 0 | 1.7908 | 0.59692 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
344 | 1 | 0 | 1.9235 | 0.64116 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
345 | 1 | 0 | 1.8231 | 0.60769 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
346 | 1 | 0 | 2.2154 | 0.73848 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
347 | 1 | 0 | 1.2348 | 0.4116 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
348 | 1 | 0 | 1.6281 | 0.54269 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
349 | 1 | 0 | 0.95797 | 0.31932 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
350 | 1 | 0 | 3.1332 | 1.0444 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
351 | 1 | 0 | 1.8294 | 0.60979 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
358 | 1 | 0 | 1.5276 | 0.5092 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
359 | 1 | 0 | 1.6957 | 0.56522 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
360 | 1 | 0 | 1.9719 | 0.65729 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
361 | 1 | 0 | 3.9741 | 1.3247 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
362 | 1 | 0 | 2.3579 | 0.78597 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
363 | 1 | 0 | 0.9652 | 0.32173 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
364 | 1 | 0 | 1.9564 | 0.65214 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
365 | 1 | 0 | 1.6777 | 0.55923 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
366 | 1 | 0 | 2.9763 | 0.99211 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
367 | 1 | 0 | 2.2385 | 0.74617 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
374 | 1 | 0 | 2.6919 | 0.89729 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
375 | 1 | 0 | 2.707 | 0.90234 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
376 | 1 | 0 | 4.8353 | 1.6118 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
377 | 1 | 0 | 5.8927 | 1.9642 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
378 | 1 | 0 | 4.091 | 1.3637 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
379 | 1 | 0 | 2.1019 | 0.70062 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
380 | 1 | 0 | 4.3646 | 1.4549 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
381 | 1 | 0 | 1.5776 | 0.52586 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
382 | 1 | 0 | 0.95572 | 0.31857 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
383 | 1 | 0 | 5.1509 | 1.7169 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
390 | 1 | 0 | 2.7695 | 0.92316 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
391 | 1 | 0 | 3.7725 | 1.2575 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
392 | 1 | 0 | 2.2839 | 0.76131 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
393 | 1 | 0 | 4.6627 | 1.5542 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
394 | 1 | 0 | 3.8182 | 1.2727 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
395 | 1 | 0 | 4.5304 | 1.5101 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
396 | 1 | 0 | 5.3545 | 1.7848 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
397 | 1 | 0 | 3.6862 | 1.2287 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
398 | 1 | 0 | 2.7373 | 0.91244 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
399 | 1 | 0 | 5.061 | 1.687 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
407 | 1 | 0 | 3.0555 | 1.0185 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
408 | 1 | 0 | 4.2399 | 1.4133 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
409 | 1 | 0 | 1.3144 | 0.43814 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
410 | 1 | 0 | 2.6832 | 0.89441 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
411 | 1 | 0 | 2.381 | 0.79366 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
412 | 1 | 0 | 2.3666 | 0.78885 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
413 | 1 | 0 | 2.5113 | 0.83711 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
414 | 1 | 0 | 7.4096 | 2.4699 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
415 | 1 | 0 | 1.1479 | 0.38263 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
416 | 1 | 0 | 0.85378 | 0.28459 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
417 | 1 | 0 | 2.4648 | 0.82159 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
418 | 1 | 0 | 1.7424 | 0.5808 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
426 | 1 | 0 | 1.7856 | 0.59519 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
427 | 1 | 0 | 2.338 | 0.77934 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
428 | 1 | 0 | 1.7375 | 0.57917 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
429 | 1 | 0 | 2.4513 | 0.81711 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
430 | 1 | 0 | 2.5421 | 0.84737 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
431 | 1 | 0 | 1.9471 | 0.64903 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
432 | 1 | 0 | 2.2534 | 0.75112 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
433 | 1 | 0 | 1.8489 | 0.61629 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
434 | 1 | 0 | 3.1846 | 1.0615 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
435 | 1 | 0 | 2.4108 | 0.8036 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
436 | 1 | 0 | 1.6512 | 0.55041 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
437 | 1 | 0 | 1.4669 | 0.48897 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
445 | 1 | 0 | 1.7596 | 0.58654 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
446 | 1 | 0 | 2.4113 | 0.80376 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
447 | 1 | 0 | 2.3262 | 0.77538 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
448 | 1 | 0 | 2.7196 | 0.90654 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
449 | 1 | 0 | 2.066 | 0.68868 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
450 | 1 | 0 | 2.2138 | 0.73794 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
451 | 1 | 0 | 1.6648 | 0.55494 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
452 | 1 | 0 | 1.6041 | 0.53471 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
453 | 1 | 0 | 2.3061 | 0.7687 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
454 | 1 | 0 | 1.401 | 0.46699 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
455 | 1 | 0 | 4.2857 | 1.4286 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
456 | 1 | 0 | 1.9204 | 0.64015 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
464 | 1 | 0 | 1.9112 | 0.63706 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
465 | 1 | 0 | 2.4547 | 0.81823 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
466 | 1 | 0 | 1.7072 | 0.56907 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
467 | 1 | 0 | 1.8114 | 0.60378 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
468 | 1 | 0 | 7.3048 | 2.4349 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
469 | 1 | 0 | 1.8229 | 0.60764 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
470 | 1 | 0 | 2.605 | 0.86833 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
471 | 1 | 0 | 1.7353 | 0.57845 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
472 | 1 | 0 | 1.7317 | 0.57722 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
473 | 1 | 0 | 1.656 | 0.55199 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
474 | 1 | 0 | 3.423 | 1.141 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
475 | 1 | 0 | 4.7388 | 1.5796 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
483 | 1 | 0 | 2.1852 | 0.72839 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
484 | 1 | 0 | 2.9762 | 0.99208 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
485 | 1 | 0 | 1.7437 | 0.58125 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
486 | 1 | 0 | 2.7302 | 0.91005 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
487 | 1 | 0 | 1.9973 | 0.66576 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
488 | 1 | 0 | 2.9842 | 0.99475 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
489 | 1 | 0 | 1.5439 | 0.51463 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
490 | 1 | 0 | 4.8828 | 1.6276 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
491 | 1 | 0 | 2.355 | 0.78498 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
492 | 1 | 0 | 1.3563 | 0.45209 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
493 | 1 | 0 | 1.3952 | 0.46506 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
494 | 1 | 0 | 1.3298 | 0.44327 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
502 | 1 | 0 | 1.6533 | 0.55109 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
503 | 1 | 0 | 1.2375 | 0.41252 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
504 | 1 | 0 | 3.9861 | 1.3287 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
505 | 1 | 0 | 3.8545 | 1.2848 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
506 | 1 | 0 | 2.29 | 0.76334 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
507 | 1 | 0 | 4.7246 | 1.5749 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
508 | 1 | 0 | 2.3815 | 0.79385 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
509 | 1 | 0 | 2.9798 | 0.99326 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
510 | 1 | 0 | 1.6713 | 0.5571 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
511 | 1 | 0 | 2.1065 | 0.70218 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
512 | 1 | 0 | 2.485 | 0.82832 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
513 | 1 | 0 | 2.7418 | 0.91394 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
521 | 1 | 0 | 1.7218 | 0.57394 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
522 | 1 | 0 | 1.8484 | 0.61615 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
523 | 1 | 0 | 1.5372 | 0.51239 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
524 | 1 | 0 | 2.6633 | 0.88777 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
525 | 1 | 0 | 3.2482 | 1.0827 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
526 | 1 | 0 | 1.656 | 0.55201 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
527 | 1 | 0 | 1.2624 | 0.4208 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
528 | 1 | 0 | 1.2725 | 0.42417 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
529 | 1 | 0 | 3.4045 | 1.1348 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
530 | 1 | 0 | 8.9949 | 2.9983 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
531 | 1 | 0 | 3.7897 | 1.2632 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
532 | 1 | 0 | 1.9117 | 0.63724 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
540 | 1 | 0 | 1.3481 | 0.44936 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
541 | 1 | 0 | 2.9142 | 0.97141 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
542 | 1 | 0 | 2.5212 | 0.84041 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
543 | 1 | 0 | 2.0314 | 0.67712 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
544 | 1 | 0 | 3.9185 | 1.3062 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
545 | 1 | 0 | 2.4042 | 0.80139 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
546 | 1 | 0 | 7.0137 | 2.3379 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
547 | 1 | 0 | 2.7447 | 0.91492 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
548 | 1 | 0 | 2.9064 | 0.96882 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
549 | 1 | 0 | 2.841 | 0.94699 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
550 | 1 | 0 | 3.9339 | 1.3113 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
551 | 1 | 0 | 3.626 | 1.2087 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
557 | 1 | 0 | 1.4938 | 0.49793 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
558 | 1 | 0 | 2.1473 | 0.71578 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
559 | 1 | 0 | 2.5079 | 0.83597 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
560 | 1 | 0 | 2.3849 | 0.79498 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
561 | 1 | 0 | 2.6441 | 0.88136 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
562 | 1 | 0 | 2.0945 | 0.69816 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
563 | 1 | 0 | 1.7842 | 0.59474 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
564 | 1 | 0 | 7.351 | 2.4503 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
570 | 1 | 0 | 4.1452 | 1.3817 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
571 | 1 | 0 | 1.377 | 0.45899 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
572 | 1 | 0 | 1.8535 | 0.61784 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
573 | 1 | 0 | 3.9045 | 1.3015 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
574 | 1 | 0 | 6.7805 | 2.2602 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
575 | 1 | 0 | 1.8296 | 0.60985 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
576 | 1 | 0 | 1.9692 | 0.65639 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
577 | 1 | 0 | 3.9619 | 1.3206 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
583 | 1 | 0 | 1.3664 | 0.45546 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
584 | 1 | 0 | 1.8785 | 0.62618 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
585 | 1 | 0 | 1.0802 | 0.36008 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
586 | 1 | 0 | 2.5293 | 0.84308 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
587 | 1 | 0 | 1.8511 | 0.61703 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
588 | 1 | 0 | 5.291 | 1.7637 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
589 | 1 | 0 | 5.5582 | 1.8527 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
590 | 1 | 0 | 2.0969 | 0.69896 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
598 | 1 | 0 | 5.7081 | 1.9027 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
599 | 1 | 0 | 5.3437 | 1.7812 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
600 | 1 | 0 | 5.6258 | 1.8753 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
601 | 1 | 0 | 1.9117 | 0.63722 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
602 | 1 | 0 | 7.1891 | 2.3964 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
603 | 1 | 0 | 3.5862 | 1.1954 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
604 | 1 | 0 | 2.0751 | 0.69171 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
605 | 1 | 0 | 3.6991 | 1.233 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
606 | 1 | 0 | 2.4843 | 0.82811 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
607 | 1 | 0 | 2.3319 | 0.77732 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
608 | 1 | 0 | 5.5577 | 1.8526 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
609 | 1 | 0 | 2.189 | 0.72968 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
617 | 1 | 0 | 6.2279 | 2.076 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
618 | 1 | 0 | 4.1947 | 1.3982 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
619 | 1 | 0 | 6.3622 | 2.1207 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
620 | 1 | 0 | 1.5589 | 0.51962 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
621 | 1 | 0 | 1.8034 | 0.60115 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
622 | 1 | 0 | 6.7702 | 2.2567 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
623 | 1 | 0 | 0.94137 | 0.31379 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
624 | 1 | 0 | 1.0193 | 0.33976 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
625 | 1 | 0 | 3.4884 | 1.1628 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
626 | 1 | 0 | 1.8653 | 0.62176 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
627 | 1 | 0 | 5.1272 | 1.7091 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
628 | 1 | 0 | 5.2396 | 1.7465 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
636 | 1 | 0 | 7.4071 | 2.469 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
637 | 1 | 0 | 1.4486 | 0.48286 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
638 | 1 | 0 | 1.4481 | 0.48269 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
639 | 1 | 0 | 1.1949 | 0.39829 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
640 | 1 | 0 | 9.8294 | 3.2765 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
641 | 1 | 0 | 4.394 | 1.4647 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
642 | 1 | 0 | 4.6715 | 1.5572 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
643 | 1 | 0 | 2.7966 | 0.93219 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
644 | 1 | 0 | 1.6513 | 0.55042 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
645 | 1 | 0 | 1.3774 | 0.45912 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
646 | 1 | 0 | 1.2733 | 0.42442 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
647 | 1 | 0 | 2.1227 | 0.70758 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
654 | 1 | 0 | 1.645 | 0.54834 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
655 | 1 | 0 | 1.1291 | 0.37637 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
656 | 1 | 0 | 2.1678 | 0.72261 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
657 | 1 | 0 | 2.2502 | 0.75006 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
658 | 1 | 0 | 1.5369 | 0.5123 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
659 | 1 | 0 | 1.0727 | 0.35756 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
660 | 1 | 0 | 2.6274 | 0.87581 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
661 | 1 | 0 | 0.65147 | 0.21716 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
662 | 1 | 0 | 1.2877 | 0.42924 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
663 | 1 | 0 | 1.364 | 0.45466 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
670 | 1 | 0 | 0.68642 | 0.22881 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
671 | 1 | 0 | 1.3792 | 0.45974 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
672 | 1 | 0 | 2.953 | 0.98434 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
673 | 1 | 0 | 1.3341 | 0.4447 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
674 | 1 | 0 | 5.1677 | 1.7226 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
675 | 1 | 0 | 3.1159 | 1.0386 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
676 | 1 | 0 | 0.68738 | 0.22913 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
677 | 1 | 0 | 2.4447 | 0.81488 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
678 | 1 | 0 | 2.2612 | 0.75372 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
679 | 1 | 0 | 2.7887 | 0.92956 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
687 | 1 | 0 | 4.4402 | 1.4801 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
688 | 1 | 0 | 2.3556 | 0.78522 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
689 | 1 | 0 | 0.92425 | 0.30808 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
690 | 1 | 0 | 2.5165 | 0.83882 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
691 | 1 | 0 | 2.438 | 0.81266 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
692 | 1 | 0 | 2.9533 | 0.98444 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
693 | 1 | 0 | 1.5118 | 0.50392 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
694 | 1 | 0 | 2.2035 | 0.73448 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
695 | 1 | 0 | 2.629 | 0.87633 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
696 | 1 | 0 | 1.3911 | 0.46369 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
697 | 1 | 0 | 2.2088 | 0.73628 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
698 | 1 | 0 | 1.9866 | 0.66219 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
706 | 1 | 0 | 1.7659 | 0.58862 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
707 | 1 | 0 | 2.1328 | 0.71094 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
708 | 1 | 0 | 1.3819 | 0.46064 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
709 | 1 | 0 | 3.0164 | 1.0055 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
710 | 1 | 0 | 2.179 | 0.72634 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
711 | 1 | 0 | 3.1971 | 1.0657 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
712 | 1 | 0 | 1.685 | 0.56167 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
713 | 1 | 0 | 2.6078 | 0.86927 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
714 | 1 | 0 | 2.6271 | 0.87572 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
715 | 1 | 0 | 1.6013 | 0.53376 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
716 | 1 | 0 | 1.6874 | 0.56248 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
717 | 1 | 0 | 2.0992 | 0.69972 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
723 | 1 | 0 | 1.5845 | 0.52816 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
724 | 1 | 0 | 1.6047 | 0.5349 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
725 | 1 | 0 | 1.502 | 0.50067 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
726 | 1 | 0 | 2.1311 | 0.71036 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
727 | 1 | 0 | 1.9909 | 0.66365 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
728 | 1 | 0 | 2.4154 | 0.80514 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
729 | 1 | 0 | 2.2648 | 0.75493 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
730 | 1 | 0 | 2.7053 | 0.90176 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
Note on B1: Author: 0- Delta 1- Star
Note on C1: Author: 0 - PQ load 1 - Const Current 2 - Const Z
Note on M1: Author: 0- kW & kVAr 1- KW & pf 2- kVA & pf
Note on N1: Author: 1- Inservice 0-out of service

## Caps
Node | Cap Type | Cap Model | kVLN | Ph1_kW | Ph1_kVAr | Ph2_kW | Ph2_kVAr | Ph3_kW | Ph3_kVAr | Status | CapControl | EachBank | Ph1 | Ph2 | Ph3
4 | 1 | 0 | 2.4018 | 0 | 200 | 0 | 200 | 0 | 200 | 0 | 1 | 20 | 10 | 10 | 10
Note on B1: Author: 0- Delta 1- Star
Note on C1: Author: 0 - Three Phase 1 - Two Phase 2 - Single Phase
Note on E1: Author: 0 - no loss
Note on L1: 0-Fixed capacitor, rated kVAR entered in CapsD(6,8,10) 1- based on taps, taps on Ph1 times each bank capacity

## Regulator
Regulator ID | From Node | To Node | Location | Regulated mode | Type | Configuration | Monitoring Phase | Bandwidth: | PT Ratio | Primary CT Rating | Vmin | Vmax | No of Steps | Tap A | Tap B | Tap C | Tap setting | Compensator Settings a | Compensator Settings b | Compensator Settings c | R - Setting | X - Setting | R - Setting | X - Setting | R - Setting | X - Setting | Voltage Level | status | CTs
0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 20 | 700 | 120 | 122 | 40 | 10 | 8 | 11 | 0 | 0 | 0 | 0 | 3 | 9 | 3 | 9 | 3 | 9 | 122 | 0 | 0
Note on D1: Author: bus no from which the bus voltage is extracted 0 - from bus 1- To bus
Note on E1: Author: 1- To bus mode 2- Based on r x setting
Note on F1: Author: 0-Type A 1- Type B
Note on G1: Author: 0- single 1- three phase 2- open delta (not modeled)
Note on H1: Author: Not used
Note on R1: Author: 0- Tap settings are forced 1- Tap settings are free to change 2- tap settings are forced but allow during optimization
Note on S1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on T1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on U1: Author: 0- R- X settings from data 1- Line Id (r and x need to be fetched)
Note on AC1: Author: 0- in service 1- by pass 2 - out of service (open in ckt)

## Cable
No | Phase Cond. | Diameter over Insulation (inch) | Diameter overScreen (inch) | Outside Diameter (inch)/Jacket Thickness (mils) | Copper 1/3 Neutral / Outside Diameter (inch) | Ampacity | Type
1 | 2 (7x) | 0.78 | 0.85 | 0.98 | 6 x 14 | 135 | 0
2 | 1/0 (19x) | 0.85 | 0.93 | 1.06 | 6 x 14 | 175 | 0
3 | 2/0 (19x) | 0.9 | 0.97 | 1.1 | 7 x 14 | 200 | 0
4 | 250 (37x) | 1.06 | 1.16 | 1.29 | 13 x 14 | 260 | 0
5 | 500 (37x) | 1.29 | 1.39 | 1.56 | 16 x 12 | 385 | 0
6 | 1000 (61x) | 1.64 | 1.77 | 1.98 | 20 x 10 | 550 | 0
7 | 1/0 AL | 0.82 | 0.88 | 80 | 1.06 | 165 | 1
Note on A1: Concentric Neutral 15 kV All Aluminum (AA) Cable - 1/3 Neutral Tape Shielded 15 kV All Aluminum (AA) Cable - Tape Thickness = 5 mils

## UDB_trafo
Config. | R11 | X11 | R12 | X12 | R13 | X13 | R22 | X22 | R23 | X23 | R33 | X33
101 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 0.0143 | 0.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## UDB_Line
Config. | R11 | X11 | R12 | X12 | R13 | X13 | R22 | X22 | R23 | X23 | R33 | X33 | Y11 | Y12 | Y13 | Y22 | Y23 | Y33 | Name
20 | 0.2926 | 0.1973 | 0.0673 | -0.0368 | 0.0337 | -0.0417 | 0.2646 | 0.19 | 0.0673 | -0.0368 | 0.2926 | 0.1973 | 159.7919 | 0 | 0 | 159.7919 | 0 | 159.7919 | 721
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4884 | 11.1975 | 127.8306 | 0 | 0 | 127.8306 | 0 | 127.8306 | 722
22 | 1.2936 | 0.6713 | 0.4871 | 0.2111 | 0.4585 | 0.1521 | 1.3022 | 0.6326 | 0.4871 | 0.2111 | 1.2936 | 0.6713 | 74.8405 | 0 | 0 | 74.8405 | 0 | 74.8405 | 723
23 | 2.0952 | 0.7758 | 0.5204 | 0.2768 | 0.4926 | 0.2123 | 2.1068 | 0.7398 | 0.5204 | 0.2738 | 2.0952 | 0.7758 | 60.248 | 0 | 0 | 60.2483 | 0 | 60.2483 | 724
50 | 0.023205 | 0.029764 | 0 | 0 | 0.0013003 | 0.007994 | 0 | 0 | 0 | 0 | 0.023205 | 0.029764 | 0 | 0 | 0 | 0 | 0 | 0 | 0
51 | 0.0088686 | 0.041313 | 0.0020849 | 0.015892 | 0.0020817 | 0.012798 | 0.0042213 | 0.038038 | 0.0020849 | 0.015892 | 0.0088686 | 0.041313 | 0 | 0 | 0 | 0 | 0 | 0 | 0
52 | 0.0044925 | 0.027695 | 0.0016038 | 0.011254 | 0.0016002 | 0.0091507 | 0.0030538 | 0.026276 | 0.0016038 | 0.011254 | 0.0044925 | 0.027695 | 0 | 0 | 0 | 0 | 0 | 0 | 0
53 | 0.002968 | 0.018297 | 0.0010596 | 0.0074352 | 0.0010572 | 0.0060455 | 0.0020175 | 0.017359 | 0.0010596 | 0.0074352 | 0.002968 | 0.018297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
54 | 0.003525 | 0.021731 | 0.0012584 | 0.0088305 | 0.0012556 | 0.0071801 | 0.0023962 | 0.020617 | 0.0012584 | 0.0088305 | 0.003525 | 0.021731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 0.0038096 | 0.023486 | 0.00136 | 0.0095434 | 0.001357 | 0.0077598 | 0.0025896 | 0.022282 | 0.00136 | 0.0095434 | 0.0038096 | 0.023486 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
57 | 0.0082434 | 0.050819 | 0.0029428 | 0.02065 | 0.0029363 | 0.016791 | 0.0056035 | 0.048214 | 0.0029428 | 0.02065 | 0.0082434 | 0.050819 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 0.00047709 | 0.0030177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59 | 0.00083826 | 0.0053022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0.0048956 | 0.030966 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | 0.0030658 | 0.019392 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | 0.0030326 | 0.019182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 0.0041132 | 0.026017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 0.0040762 | 0.025783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | 0.0052171 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 0.0045126 | 0.028543 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0.0044785 | 0.028328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
68 | 0.0025655 | 0.00096719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | 0.042635 | 0.016073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 | 0.0061134 | 0.028479 | 0.0014372 | 0.010955 | 0.001435 | 0.008822 | 0.00438 | 0.027418 | 0.0014372 | 0.010955 | 0.0061134 | 0.028479 | 0 | 0 | 0 | 0 | 0 | 0 | 0
71 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0 | 0 | 0 | 0 | 0 | 0 | 0
72 | 0.0010253 | 0.00024582 | 0.00025839 | 6.4829e-05 | 0.00025839 | 6.4829e-05 | 0.0010253 | 0.00024582 | 0.00025839 | 6.4829e-05 | 0.0010253 | 0.00024582 | 0 | 0 | 0 | 0 | 0 | 0 | 0
73 | 0.0081542 | 0.001955 | 0.0020549 | 0.00051557 | 0.0020549 | 0.00051557 | 0.0081542 | 0.001955 | 0.0020549 | 0.00051557 | 0.0081542 | 0.001955 | 0 | 0 | 0 | 0 | 0 | 0 | 0
74 | 0.048493 | 0.013265 | 0.012406 | 0.0011258 | 0.012406 | 0.0011258 | 0.048493 | 0.013265 | 0.012406 | 0.0011258 | 0.048493 | 0.013265 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 | 0.055849 | 0.01339 | 0.014074 | 0.0035312 | 0.014074 | 0.0035312 | 0.055849 | 0.01339 | 0.014074 | 0.0035312 | 0.055849 | 0.01339 | 0 | 0 | 0 | 0 | 0 | 0 | 0
76 | 8.7379e-05 | 0.0005527 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 8.7471e-05 | 0.00054755 | 2.8701e-05 | 0.00021878 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | 0.0062563 | 0.039573 | 0.002055 | 0.015665 | 0.0020519 | 0.012615 | 0.0062629 | 0.039204 | 0.002055 | 0.015665 | 0.0062563 | 0.039573 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055229 | 0.034934 | 0 | 0 | 0 | 0 | 0 | 0 | 0
79 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0020473 | 0.01295 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0084702 | 0.053577 | 0 | 0 | 0 | 0 | 0 | 0 | 0
81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0080986 | 0.051226 | 0 | 0 | 0 | 0 | 0 | 0 | 0
82 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0071887 | 0.045471 | 0 | 0 | 0 | 0 | 0 | 0 | 0
83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072059 | 0.045579 | 0 | 0 | 0 | 0 | 0 | 0 | 0
84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014563 | 0.00092117 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012924 | 0.00053241 | 0 | 0 | 0 | 0 | 0 | 0 | 0
87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03114 | 0.012828 | 0 | 0 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.040892 | 0.016846 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0036855 | 0.0015183 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.034356 | 0.014153 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.066083 | 0.027224 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049012 | 0.020191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027042 | 0.01114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
94 | 0.0079847 | 0.049224 | 0.0028505 | 0.020002 | 0.0028442 | 0.016264 | 0.0054276 | 0.046701 | 0.0028505 | 0.020002 | 0.0079847 | 0.049224 | 0 | 0 | 0 | 0 | 0 | 0 | 0
95 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 | 0.0020197 | 0.00083202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
97 | 0.053479 | 0.022031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
98 | 0.096145 | 0.039608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | 0.0035317 | 0.021772 | 0.0012608 | 0.0088473 | 0.001258 | 0.0071937 | 0.0024007 | 0.020656 | 0.0012608 | 0.0088473 | 0.0035317 | 0.021772 | 0 | 0 | 0 | 0 | 0 | 0 | 0
100 | 0.0044001 | 0.038301 | 0.0023163 | 0.016254 | 0.0023112 | 0.013216 | 0.006499 | 0.03965 | 0.0023163 | 0.016254 | 0.0064885 | 0.040001 | 0 | 0 | 0 | 0 | 0 | 0 | 0
101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0024425 | 0.01545 | 0 | 0 | 0 | 0 | 0 | 0 | 0
102 | 0.0034016 | 0.02097 | 0.0012143 | 0.0085213 | 0.0012117 | 0.0069287 | 0.0023123 | 0.019895 | 0.0012143 | 0.0085213 | 0.0034016 | 0.02097 | 0 | 0 | 0 | 0 | 0 | 0 | 0
103 | 0.0036205 | 0.02232 | 0.0012925 | 0.0090697 | 0.0012896 | 0.0073746 | 0.0024611 | 0.021176 | 0.0012925 | 0.0090697 | 0.0036205 | 0.02232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
104 | 0.0047859 | 0.029504 | 0.0017085 | 0.011989 | 0.0017047 | 0.0097483 | 0.0032532 | 0.027992 | 0.0017085 | 0.011989 | 0.0047859 | 0.029504 | 0 | 0 | 0 | 0 | 0 | 0 | 0
105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052678 | 0.0021701 | 0 | 0 | 0 | 0 | 0 | 0 | 0
107 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061216 | 0.025219 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.07911 | 0.03259 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.074872 | 0.030844 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052506 | 0.002163 | 0 | 0 | 0 | 0 | 0 | 0 | 0
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.10989 | 0.045269 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025995 | 0.010709 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.064887 | 0.026731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061005 | 0.025132 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.056123 | 0.02312 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | 0.0032249 | 0.019881 | 0.0011513 | 0.0080788 | 0.0011487 | 0.0065689 | 0.0021922 | 0.018862 | 0.0011513 | 0.0080788 | 0.0032249 | 0.019881 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 0.0034551 | 0.0213 | 0.0012334 | 0.0086553 | 0.0012307 | 0.0070377 | 0.0023486 | 0.020208 | 0.0012334 | 0.0086553 | 0.0034551 | 0.0213 | 0 | 0 | 0 | 0 | 0 | 0 | 0
119 | 0.0035001 | 0.021578 | 0.0012495 | 0.0087681 | 0.0012467 | 0.0071293 | 0.0023792 | 0.020471 | 0.0012495 | 0.0087681 | 0.0035001 | 0.021578 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0.0035259 | 0.021737 | 0.0012587 | 0.0088328 | 0.001256 | 0.007182 | 0.0023968 | 0.020623 | 0.0012587 | 0.0088328 | 0.0035259 | 0.021737 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0
122 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
123 | 0.0012678 | 0.00052229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
124 | 0.074899 | 0.030856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | 0.037656 | 0.015513 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
126 | 0.028307 | 0.011661 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | 0.018688 | 0.0076987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 0.066818 | 0.027526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013022 | 0.00053646 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.023049 | 0.0094953 | 0 | 0 | 0 | 0 | 0 | 0 | 0
131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.089334 | 0.036802 | 0 | 0 | 0 | 0 | 0 | 0 | 0
132 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.061781 | 0.025451 | 0 | 0 | 0 | 0 | 0 | 0 | 0
133 | 0.004145 | 0.025553 | 0.0014797 | 0.010384 | 0.0014764 | 0.0084428 | 0.0028176 | 0.024243 | 0.0014797 | 0.010384 | 0.004145 | 0.025553 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | 0.0050049 | 0.0020618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
136 | 0.063074 | 0.025984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | 0.0036506 | 0.022505 | 0.0013032 | 0.0091451 | 0.0013004 | 0.0074359 | 0.0024815 | 0.021352 | 0.0013032 | 0.0091451 | 0.0036506 | 0.022505 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 0.0035186 | 0.021692 | 0.0012561 | 0.0088145 | 0.0012534 | 0.0071671 | 0.0023918 | 0.02058 | 0.0012561 | 0.0088145 | 0.0035186 | 0.021692 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 0.0033321 | 0.00091151 | 0.00085243 | 7.7361e-05 | 0.00085243 | 7.7361e-05 | 0.0033321 | 0.00091151 | 0.00085243 | 7.7361e-05 | 0.0033321 | 0.00091151 | 0 | 0 | 0 | 0 | 0 | 0 | 0
141 | 0.028431 | 0.0077774 | 0.0072733 | 0.00066008 | 0.0072733 | 0.00066008 | 0.028431 | 0.0077774 | 0.0072733 | 0.00066008 | 0.028431 | 0.0077774 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 0.0040699 | 0.023281 | 0.0011406 | 0.0086943 | 0.0011389 | 0.0070015 | 0.0018673 | 0.019831 | 0.0011406 | 0.0086943 | 0.0040699 | 0.023281 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | 0.0038576 | 0.022066 | 0.0010811 | 0.0082407 | 0.0010794 | 0.0066362 | 0.0017699 | 0.018796 | 0.0010811 | 0.0082407 | 0.0038576 | 0.022066 | 0 | 0 | 0 | 0 | 0 | 0 | 0
144 | 0.0038794 | 0.022191 | 0.0010872 | 0.0082874 | 0.0010855 | 0.0066738 | 0.0017799 | 0.018903 | 0.0010872 | 0.0082874 | 0.0038794 | 0.022191 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | 0.0042775 | 0.024468 | 0.0011988 | 0.0091377 | 0.0011969 | 0.0073586 | 0.0019625 | 0.020842 | 0.0011988 | 0.0091377 | 0.0042775 | 0.024468 | 0 | 0 | 0 | 0 | 0 | 0 | 0
146 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | 0.017184 | 0.010433 | 0.012836 | 0.0024936 | 0.012836 | 0.0024936 | 0.017184 | 0.010433 | 0.012836 | 0.0024936 | 0.017184 | 0.010433 | 0 | 0 | 0 | 0 | 0 | 0 | 0
148 | 0.0034005 | 0.019451 | 0.00095298 | 0.0072642 | 0.00095153 | 0.0058498 | 0.0015602 | 0.016569 | 0.00095298 | 0.0072642 | 0.0034005 | 0.019451 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | 0.0007371 | 0.00030366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0.090044 | 0.037095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
151 | 0.04954 | 0.020409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 0.0040088 | 0.022931 | 0.0011235 | 0.0085637 | 0.0011218 | 0.0068964 | 0.0018393 | 0.019533 | 0.0011235 | 0.0085637 | 0.0040088 | 0.022931 | 0 | 0 | 0 | 0 | 0 | 0 | 0
153 | 0.0038009 | 0.021742 | 0.0010652 | 0.0081196 | 0.0010636 | 0.0065387 | 0.0017439 | 0.01852 | 0.0010652 | 0.0081196 | 0.0038009 | 0.021742 | 0 | 0 | 0 | 0 | 0 | 0 | 0
154 | 0.00010241 | 0.00058582 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 4.6988e-05 | 0.00049902 | 2.8701e-05 | 0.00021878 | 0.00010241 | 0.00058582 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0.0010541 | 0.015854 | 0.00063209 | 0.006817 | 0.00063348 | 0.0054459 | 0.0010514 | 0.015682 | 0.00063209 | 0.006817 | 0.0010541 | 0.015854 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | 0.0014203 | 0.021362 | 0.00085169 | 0.0091854 | 0.00085357 | 0.007338 | 0.0014167 | 0.02113 | 0.00085169 | 0.0091854 | 0.0014203 | 0.021362 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | 0.00064333 | 0.009676 | 0.00038577 | 0.0041605 | 0.00038662 | 0.0033237 | 0.00064169 | 0.009571 | 0.00038577 | 0.0041605 | 0.00064333 | 0.009676 | 0 | 0 | 0 | 0 | 0 | 0 | 0
158 | 0.0010782 | 0.016216 | 0.00064652 | 0.0069727 | 0.00064795 | 0.0055703 | 0.0010754 | 0.01604 | 0.00064652 | 0.0069727 | 0.0010782 | 0.016216 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 7.015e-05 | 0.0010551 | 4.2065e-05 | 0.00045367 | 4.2158e-05 | 0.00036242 | 6.9971e-05 | 0.0010436 | 4.2065e-05 | 0.00045367 | 7.015e-05 | 0.0010551 | 0 | 0 | 0 | 0 | 0 | 0 | 0
160 | 0.0015598 | 0.023459 | 0.00093529 | 0.010087 | 0.00093736 | 0.0080583 | 0.0015558 | 0.023205 | 0.00093529 | 0.010087 | 0.0015598 | 0.023459 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | 0.0011637 | 0.017502 | 0.0006978 | 0.0075257 | 0.00069934 | 0.0060121 | 0.0011607 | 0.017312 | 0.0006978 | 0.0075257 | 0.0011637 | 0.017502 | 0 | 0 | 0 | 0 | 0 | 0 | 0
162 | 0.0013849 | 0.02083 | 0.00083046 | 0.0089564 | 0.00083229 | 0.0071551 | 0.0013814 | 0.020604 | 0.00083046 | 0.0089564 | 0.0013849 | 0.02083 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | 6.5675e-05 | 0.00053684 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 6.5766e-05 | 0.00053169 | 2.8701e-05 | 0.00021878 | 6.5675e-05 | 0.00053684 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 0.010999 | 0.0066774 | 0.0082156 | 0.001596 | 0.0082156 | 0.001596 | 0.010999 | 0.0066774 | 0.0082156 | 0.001596 | 0.010999 | 0.0066774 | 0 | 0 | 0 | 0 | 0 | 0 | 0
165 | 0.024205 | 0.014696 | 0.018081 | 0.0035124 | 0.018081 | 0.0035124 | 0.024205 | 0.014696 | 0.018081 | 0.0035124 | 0.024205 | 0.014696 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | 0.029391 | 0.017844 | 0.021955 | 0.0042649 | 0.021955 | 0.0042649 | 0.029391 | 0.017844 | 0.021955 | 0.0042649 | 0.029391 | 0.017844 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | 0.039457 | 0.023955 | 0.029473 | 0.0057255 | 0.029473 | 0.0057255 | 0.039457 | 0.023955 | 0.029473 | 0.0057255 | 0.039457 | 0.023955 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | 0.034549 | 0.020975 | 0.025807 | 0.0050133 | 0.025807 | 0.0050133 | 0.034549 | 0.020975 | 0.025807 | 0.0050133 | 0.034549 | 0.020975 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | 0.034679 | 0.021054 | 0.025905 | 0.0050323 | 0.025905 | 0.0050323 | 0.034679 | 0.021054 | 0.025905 | 0.0050323 | 0.034679 | 0.021054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | 0.043774 | 0.026576 | 0.032698 | 0.006352 | 0.032698 | 0.006352 | 0.043774 | 0.026576 | 0.032698 | 0.006352 | 0.043774 | 0.026576 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 0.030863 | 0.018737 | 0.023054 | 0.0044785 | 0.023054 | 0.0044785 | 0.030863 | 0.018737 | 0.023054 | 0.0044785 | 0.030863 | 0.018737 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | 0.010882 | 0.0066069 | 0.0081289 | 0.0015791 | 0.0081289 | 0.0015791 | 0.010882 | 0.0066069 | 0.0081289 | 0.0015791 | 0.010882 | 0.0066069 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0.019494 | 0.011835 | 0.014561 | 0.0028287 | 0.014561 | 0.0028287 | 0.019494 | 0.011835 | 0.014561 | 0.0028287 | 0.019494 | 0.011835 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0.039917 | 0.024234 | 0.029817 | 0.0057923 | 0.029817 | 0.0057923 | 0.039917 | 0.024234 | 0.029817 | 0.0057923 | 0.039917 | 0.024234 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0.020241 | 0.012288 | 0.015119 | 0.0029371 | 0.015119 | 0.0029371 | 0.020241 | 0.012288 | 0.015119 | 0.0029371 | 0.020241 | 0.012288 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0.005408 | 0.0032833 | 0.0040396 | 0.00078474 | 0.0040396 | 0.00078474 | 0.005408 | 0.0032833 | 0.0040396 | 0.00078474 | 0.005408 | 0.0032833 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0.00072194 | 0.0004383 | 0.00053927 | 0.00010476 | 0.00053927 | 0.00010476 | 0.00072194 | 0.0004383 | 0.00053927 | 0.00010476 | 0.00072194 | 0.0004383 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 4.6582e-05 | 0.00050177 | 2.8387e-05 | 0.00021636 | 2.8344e-05 | 0.00017379 | 4.6674e-05 | 0.00049657 | 2.8387e-05 | 0.00021636 | 4.6582e-05 | 0.00050177 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | 0.0015641 | 0.016848 | 0.00095315 | 0.0072645 | 0.00095168 | 0.0058351 | 0.0015671 | 0.016673 | 0.00095315 | 0.0072645 | 0.0015641 | 0.016848 | 0 | 0 | 0 | 0 | 0 | 0 | 0
180 | 0.062263 | 0.014927 | 0.015691 | 0.0039368 | 0.015691 | 0.0039368 | 0.062263 | 0.014927 | 0.015691 | 0.0039368 | 0.062263 | 0.014927 | 0 | 0 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0018586 | 0.010402 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | 0.10203 | 0.024461 | 0.025712 | 0.006451 | 0.025712 | 0.006451 | 0.10203 | 0.024461 | 0.025712 | 0.006451 | 0.10203 | 0.024461 | 0 | 0 | 0 | 0 | 0 | 0 | 0
183 | 0.024065 | 0.014611 | 0.017976 | 0.0034921 | 0.017976 | 0.0034921 | 0.024065 | 0.014611 | 0.017976 | 0.0034921 | 0.024065 | 0.014611 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0 | 0 | 0 | 0 | 0 | 0 | 0
185 | 0.0019897 | 0.021432 | 0.0012125 | 0.0092413 | 0.0012106 | 0.007423 | 0.0019936 | 0.02121 | 0.0012125 | 0.0092413 | 0.0019897 | 0.021432 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | 2.9968e-05 | 0.00032281 | 1.8262e-05 | 0.00013919 | 1.8234e-05 | 0.0001118 | 3.0027e-05 | 0.00031946 | 1.8262e-05 | 0.00013919 | 2.9968e-05 | 0.00032281 | 0 | 0 | 0 | 0 | 0 | 0 | 0
187 | 5.0211e-05 | 0.00021125 | 3.1545e-05 | 0.00010297 | 3.1336e-05 | 8.8957e-05 | 5.0631e-05 | 0.00021036 | 3.1545e-05 | 0.00010297 | 5.0211e-05 | 0.00021125 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 0.00026518 | 0.0011156 | 0.0001666 | 0.0005438 | 0.00016549 | 0.0004698 | 0.00026739 | 0.001111 | 0.0001666 | 0.0005438 | 0.00026518 | 0.0011156 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0.00025419 | 0.0010694 | 0.00015969 | 0.00052128 | 0.00015864 | 0.00045035 | 0.00025632 | 0.001065 | 0.00015969 | 0.00052128 | 0.00025419 | 0.0010694 | 0 | 0 | 0 | 0 | 0 | 0 | 0
190 | 4.2888e-05 | 0.00018044 | 2.6944e-05 | 8.7953e-05 | 2.6766e-05 | 7.5984e-05 | 4.3247e-05 | 0.00017968 | 2.6944e-05 | 8.7953e-05 | 4.2888e-05 | 0.00018044 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 3.1415e-05 | 0.00035448 | 1.8925e-05 | 0.00014424 | 1.8896e-05 | 0.00011586 | 3.1476e-05 | 0.00035101 | 1.8925e-05 | 0.00014424 | 3.1415e-05 | 0.00035448 | 0 | 0 | 0 | 0 | 0 | 0 | 0
192 | 0.0018538 | 0.020918 | 0.0011168 | 0.0085115 | 0.001115 | 0.0068367 | 0.0018574 | 0.020713 | 0.0011168 | 0.0085115 | 0.0018538 | 0.020918 | 0 | 0 | 0 | 0 | 0 | 0 | 0
193 | 0.0023446 | 0.026457 | 0.0014125 | 0.010765 | 0.0014103 | 0.008647 | 0.0023492 | 0.026198 | 0.0014125 | 0.010765 | 0.0023446 | 0.026457 | 0 | 0 | 0 | 0 | 0 | 0 | 0
194 | 0.0019837 | 0.022384 | 0.001195 | 0.0091079 | 0.0011932 | 0.0073158 | 0.0019875 | 0.022165 | 0.001195 | 0.0091079 | 0.0019837 | 0.022384 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0.0001734 | 3.3685e-05 | 0.00023213 | 0.00014093 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0.00039589 | 9.4914e-05 | 9.9766e-05 | 2.5031e-05 | 9.9766e-05 | 2.5031e-05 | 0.00039589 | 9.4914e-05 | 9.9766e-05 | 2.5031e-05 | 0.00039589 | 9.4914e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
197 | 0.034844 | 0.0083538 | 0.0087809 | 0.0022031 | 0.0087809 | 0.0022031 | 0.034844 | 0.0083538 | 0.0087809 | 0.0022031 | 0.034844 | 0.0083538 | 0 | 0 | 0 | 0 | 0 | 0 | 0
198 | 0.0022612 | 0.025516 | 0.0013622 | 0.010382 | 0.0013601 | 0.0083394 | 0.0022656 | 0.025266 | 0.0013622 | 0.010382 | 0.0022612 | 0.025516 | 0 | 0 | 0 | 0 | 0 | 0 | 0
199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019861 | 0.00062828 | 0 | 0 | 0 | 0 | 0 | 0 | 0
200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.143e-05 | 0.00025759 | 0 | 0 | 0 | 0 | 0 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054817 | 0.01734 | 0 | 0 | 0 | 0 | 0 | 0 | 0
202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0070851 | 0.022413 | 0 | 0 | 0 | 0 | 0 | 0 | 0
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098822 | 0.031261 | 0 | 0 | 0 | 0 | 0 | 0 | 0
204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004422 | 0.02797 | 0 | 0 | 0 | 0 | 0 | 0 | 0
205 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043387 | 0.027443 | 0 | 0 | 0 | 0 | 0 | 0 | 0
206 | 0.010551 | 0.0064059 | 0.0078815 | 0.0015311 | 0.0078815 | 0.0015311 | 0.010551 | 0.0064059 | 0.0078815 | 0.0015311 | 0.010551 | 0.0064059 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0.0023644 | 0.02668 | 0.0014244 | 0.010856 | 0.0014222 | 0.00872 | 0.002369 | 0.026419 | 0.0014244 | 0.010856 | 0.0023644 | 0.02668 | 0 | 0 | 0 | 0 | 0 | 0 | 0
208 | 0.0022488 | 0.025376 | 0.0013547 | 0.010325 | 0.0013526 | 0.0082936 | 0.0022532 | 0.025127 | 0.0013547 | 0.010325 | 0.0022488 | 0.025376 | 0 | 0 | 0 | 0 | 0 | 0 | 0
209 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
210 | 0.032991 | 0.01031 | 0.0084198 | 0.00085323 | 0.0084198 | 0.00085323 | 0.032991 | 0.01031 | 0.0084198 | 0.00085323 | 0.032991 | 0.01031 | 0 | 0 | 0 | 0 | 0 | 0 | 0
211 | 0.0019634 | 0.022155 | 0.0011828 | 0.0090148 | 0.001181 | 0.0072411 | 0.0019672 | 0.021938 | 0.0011828 | 0.0090148 | 0.0019634 | 0.022155 | 0 | 0 | 0 | 0 | 0 | 0 | 0
212 | 0.0054136 | 0.023552 | 0.0015707 | 0.0091379 | 0.0015649 | 0.0073814 | 0.0054254 | 0.023344 | 0.0015707 | 0.0091379 | 0.0054136 | 0.023552 | 0 | 0 | 0 | 0 | 0 | 0 | 0
213 | 0.0049997 | 0.021751 | 0.0014505 | 0.0084392 | 0.0014452 | 0.0068169 | 0.0050105 | 0.021559 | 0.0014505 | 0.0084392 | 0.0049997 | 0.021751 | 0 | 0 | 0 | 0 | 0 | 0 | 0
214 | 0.0017138 | 0.019339 | 0.0010324 | 0.0078689 | 0.0010309 | 0.0063206 | 0.0017171 | 0.01915 | 0.0010324 | 0.0078689 | 0.0017138 | 0.019339 | 0 | 0 | 0 | 0 | 0 | 0 | 0
215 | 8.7379e-05 | 0.0005527 | 2.8701e-05 | 0.00021878 | 2.8658e-05 | 0.00017618 | 8.7471e-05 | 0.00054755 | 2.8701e-05 | 0.00021878 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
216 | 2.4757e-05 | 0.0001566 | 8.1321e-06 | 6.1987e-05 | 8.1197e-06 | 4.9918e-05 | 2.4783e-05 | 0.00015514 | 8.1321e-06 | 6.1987e-05 | 2.4757e-05 | 0.0001566 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | 0.0021487 | 0.013591 | 0.00070577 | 0.0053798 | 0.00070469 | 0.0043323 | 0.0021509 | 0.013464 | 0.00070577 | 0.0053798 | 0.0021487 | 0.013591 | 0 | 0 | 0 | 0 | 0 | 0 | 0
218 | 0.0027795 | 0.017581 | 0.00091299 | 0.0069594 | 0.0009116 | 0.0056044 | 0.0027824 | 0.017418 | 0.00091299 | 0.0069594 | 0.0027795 | 0.017581 | 0 | 0 | 0 | 0 | 0 | 0 | 0
219 | 0.0027854 | 0.017618 | 0.0009149 | 0.0069739 | 0.00091351 | 0.0056161 | 0.0027883 | 0.017454 | 0.0009149 | 0.0069739 | 0.0027854 | 0.017618 | 0 | 0 | 0 | 0 | 0 | 0 | 0
220 | 0.0028468 | 0.018007 | 0.00093509 | 0.0071278 | 0.00093366 | 0.00574 | 0.0028498 | 0.017839 | 0.00093509 | 0.0071278 | 0.0028468 | 0.018007 | 0 | 0 | 0 | 0 | 0 | 0 | 0
221 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0 | 0 | 0 | 0 | 0 | 0 | 0
222 | 0.00013993 | 3.8277e-05 | 3.5796e-05 | 3.2486e-06 | 3.5796e-05 | 3.2486e-06 | 0.00013993 | 3.8277e-05 | 3.5796e-05 | 3.2486e-06 | 0.00013993 | 3.8277e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | 0.010571 | 0.0028917 | 0.0027043 | 0.00024542 | 0.0027043 | 0.00024542 | 0.010571 | 0.0028917 | 0.0027043 | 0.00024542 | 0.010571 | 0.0028917 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | 0.0019356 | 0.021841 | 0.0011661 | 0.0088872 | 0.0011643 | 0.0071385 | 0.0019394 | 0.021628 | 0.0011661 | 0.0088872 | 0.0019356 | 0.021841 | 0 | 0 | 0 | 0 | 0 | 0 | 0
225 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0.00014318 | 1.2994e-05 | 0.00055971 | 0.00015311 | 0 | 0 | 0 | 0 | 0 | 0 | 0
226 | 0.00092166 | 0.00025212 | 0.00023578 | 2.1398e-05 | 0.00023578 | 2.1398e-05 | 0.00092166 | 0.00025212 | 0.00023578 | 2.1398e-05 | 0.00092166 | 0.00025212 | 0 | 0 | 0 | 0 | 0 | 0 | 0
227 | 0.028379 | 0.0077631 | 0.00726 | 0.00065886 | 0.00726 | 0.00065886 | 0.028379 | 0.0077631 | 0.00726 | 0.00065886 | 0.028379 | 0.0077631 | 0 | 0 | 0 | 0 | 0 | 0 | 0
228 | 0.0019439 | 0.021935 | 0.0011711 | 0.0089254 | 0.0011693 | 0.0071692 | 0.0019477 | 0.021721 | 0.0011711 | 0.0089254 | 0.0019439 | 0.021935 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 0.0019659 | 0.022184 | 0.0011843 | 0.0090264 | 0.0011825 | 0.0072503 | 0.0019697 | 0.021966 | 0.0011843 | 0.0090264 | 0.0019659 | 0.022184 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
231 | 0.028673 | 0.0089608 | 0.0073176 | 0.00074154 | 0.0073176 | 0.00074154 | 0.028673 | 0.0089608 | 0.0073176 | 0.00074154 | 0.028673 | 0.0089608 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0.0085309 | 0.037114 | 0.0024751 | 0.0144 | 0.002466 | 0.011632 | 0.0085495 | 0.036786 | 0.0024751 | 0.0144 | 0.0085309 | 0.037114 | 0 | 0 | 0 | 0 | 0 | 0 | 0
233 | 0.0089497 | 0.038936 | 0.0025966 | 0.015107 | 0.002587 | 0.012203 | 0.0089692 | 0.038591 | 0.0025966 | 0.015107 | 0.0089497 | 0.038936 | 0 | 0 | 0 | 0 | 0 | 0 | 0
234 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0071571 | 0.044802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | 0.001795 | 0.020255 | 0.0010814 | 0.0082417 | 0.0010797 | 0.0066201 | 0.0017985 | 0.020057 | 0.0010814 | 0.0082417 | 0.001795 | 0.020255 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | 0.0015926 | 0.017971 | 0.00095939 | 0.0073121 | 0.00095792 | 0.0058734 | 0.0015957 | 0.017795 | 0.00095939 | 0.0073121 | 0.0015926 | 0.017971 | 0 | 0 | 0 | 0 | 0 | 0 | 0
237 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0.00021532 | 5.4024e-05 | 0.00085444 | 0.00020485 | 0 | 0 | 0 | 0 | 0 | 0 | 0
238 | 0.071488 | 0.017139 | 0.018015 | 0.00452 | 0.018015 | 0.00452 | 0.071488 | 0.017139 | 0.018015 | 0.00452 | 0.071488 | 0.017139 | 0 | 0 | 0 | 0 | 0 | 0 | 0
239 | 0.063232 | 0.017297 | 0.016176 | 0.001468 | 0.016176 | 0.001468 | 0.063232 | 0.017297 | 0.016176 | 0.001468 | 0.063232 | 0.017297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | 0.0089643 | 0.0054424 | 0.0066961 | 0.0013008 | 0.0066961 | 0.0013008 | 0.0089643 | 0.0054424 | 0.0066961 | 0.0013008 | 0.0089643 | 0.0054424 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | 0.0023907 | 0.026976 | 0.0014402 | 0.010976 | 0.001438 | 0.0088167 | 0.0023953 | 0.026712 | 0.0014402 | 0.010976 | 0.0023907 | 0.026976 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | 4.7122e-05 | 0.00053173 | 2.8387e-05 | 0.00021636 | 2.8344e-05 | 0.00017379 | 4.7213e-05 | 0.00052652 | 2.8387e-05 | 0.00021636 | 4.7122e-05 | 0.00053173 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | 3.33e-05 | 0.00037575 | 2.006e-05 | 0.00015289 | 2.0029e-05 | 0.00012281 | 3.3364e-05 | 0.00037208 | 2.006e-05 | 0.00015289 | 3.33e-05 | 0.00037575 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 0.0018938 | 0.02137 | 0.0011409 | 0.0086954 | 0.0011391 | 0.0069845 | 0.0018975 | 0.021161 | 0.0011409 | 0.0086954 | 0.0018938 | 0.02137 | 0 | 0 | 0 | 0 | 0 | 0 | 0
245 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 0.00072846 | 0.00022766 | 0.00018591 | 1.884e-05 | 0.00018591 | 1.884e-05 | 0.00072846 | 0.00022766 | 0.00018591 | 1.884e-05 | 0.00072846 | 0.00022766 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 0.030478 | 0.009525 | 0.0077784 | 0.00078823 | 0.0077784 | 0.00078823 | 0.030478 | 0.009525 | 0.0077784 | 0.00078823 | 0.030478 | 0.009525 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 0.0020131 | 0.022715 | 0.0012127 | 0.0092427 | 0.0012108 | 0.0074241 | 0.002017 | 0.022493 | 0.0012127 | 0.0092427 | 0.0020131 | 0.022715 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 0.0028738 | 0.032428 | 0.0017312 | 0.013195 | 0.0017286 | 0.010599 | 0.0028794 | 0.032111 | 0.0017312 | 0.013195 | 0.0028738 | 0.032428 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 0.0016994 | 0.018269 | 0.00104 | 0.0079278 | 0.0010385 | 0.0063843 | 0.0017027 | 0.018083 | 0.00104 | 0.0079278 | 0.0016994 | 0.018269 | 0 | 0 | 0 | 0 | 0 | 0 | 0
251 | 0.005273 | 0.033354 | 0.001732 | 0.013203 | 0.0017294 | 0.010632 | 0.0052786 | 0.033043 | 0.001732 | 0.013203 | 0.005273 | 0.033354 | 0 | 0 | 0 | 0 | 0 | 0 | 0
252 | 0.00014126 | 0.00089353 | 4.6401e-05 | 0.00035369 | 4.633e-05 | 0.00028483 | 0.00014141 | 0.0008852 | 4.6401e-05 | 0.00035369 | 0.00014126 | 0.00089353 | 0 | 0 | 0 | 0 | 0 | 0 | 0
253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030137 | 0.019063 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049943 | 0.03159 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 0.0019582 | 0.029452 | 0.0011742 | 0.012664 | 0.0011768 | 0.010117 | 0.0019532 | 0.029133 | 0.0011742 | 0.012664 | 0.0019582 | 0.029452 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 0.0016264 | 0.024462 | 0.00097527 | 0.010518 | 0.00097743 | 0.0084027 | 0.0016223 | 0.024196 | 0.00097527 | 0.010518 | 0.0016264 | 0.024462 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 0.00032837 | 0.0026842 | 0.00014351 | 0.0010939 | 0.00014329 | 0.00088091 | 0.00032883 | 0.0026585 | 0.00014351 | 0.0010939 | 0.00032837 | 0.0026842 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 0.00061196 | 0.0092042 | 0.00036696 | 0.0039576 | 0.00036777 | 0.0031616 | 0.0006104 | 0.0091043 | 0.00036696 | 0.0039576 | 0.00061196 | 0.0092042 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 0.00067129 | 0.0031187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 0.0080002 | 0.037168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
262 | 0.0068324 | 0.031743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | 0.0064389 | 0.029915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
264 | 0.0064929 | 0.030165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
265 | 0.0063207 | 0.029365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | 0.0056904 | 0.035994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
267 | 0.0062377 | 0.039455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | 0.0019317 | 0.029054 | 0.0011584 | 0.012493 | 0.0011609 | 0.0099802 | 0.0019268 | 0.028739 | 0.0011584 | 0.012493 | 0.0019317 | 0.029054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
269 | 0.0014991 | 0.022547 | 0.00089891 | 0.0096947 | 0.0009009 | 0.0077448 | 0.0014952 | 0.022302 | 0.00089891 | 0.0096947 | 0.0014991 | 0.022547 | 0 | 0 | 0 | 0 | 0 | 0 | 0
270 | 0.0012787 | 0.019232 | 0.00076677 | 0.0082696 | 0.00076847 | 0.0066064 | 0.0012754 | 0.019024 | 0.00076677 | 0.0082696 | 0.0012787 | 0.019232 | 0 | 0 | 0 | 0 | 0 | 0 | 0
271 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7471e-05 | 0.00054755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
272 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00017407 | 0.0010896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0037583 | 0.023526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
274 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043254 | 0.027076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
275 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0034945 | 0.021875 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
276 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005101 | 0.031931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
277 | 0 | 0 | 0 | 0 | 0 | 0 | 0.007414 | 0.04641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0056623 | 0.035445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
279 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019775 | 0.00058189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
280 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093556 | 0.027529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
281 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0061079 | 0.017973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098196 | 0.028895 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
283 | 0 | 0 | 0 | 0 | 0 | 0 | 0.009697 | 0.028534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
284 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010302 | 0.030315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
285 | 0 | 0 | 0 | 0 | 0 | 0 | 0.013107 | 0.038568 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012158 | 0.035775 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
287 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010555 | 0.031058 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
288 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010003 | 0.029434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
289 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0091453 | 0.026911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
290 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0098446 | 0.042358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013171 | 0.00056669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026078 | 0.001122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064966 | 0.027953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
294 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0063825 | 0.027462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0042677 | 0.026715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
296 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0043295 | 0.027102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
297 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00065633 | 0.002824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
298 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049877 | 0.02146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065129 | 0.028023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
300 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0053846 | 0.023168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0073444 | 0.0316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0064092 | 0.027577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065225 | 0.028064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
304 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0062165 | 0.026748 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | 0.0014429 | 0.021701 | 0.00086521 | 0.0093312 | 0.00086712 | 0.0074545 | 0.0014392 | 0.021466 | 0.00086521 | 0.0093312 | 0.0014429 | 0.021701 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | 0.00032837 | 0.0026842 | 0.00014351 | 0.0010939 | 0.00014329 | 0.00088091 | 0.00032883 | 0.0026585 | 0.00014351 | 0.0010939 | 0.00032837 | 0.0026842 | 0 | 0 | 0 | 0 | 0 | 0 | 0
307 | 0.0015636 | 0.023517 | 0.00093758 | 0.010112 | 0.00093965 | 0.008078 | 0.0015596 | 0.023261 | 0.00093758 | 0.010112 | 0.0015636 | 0.023517 | 0 | 0 | 0 | 0 | 0 | 0 | 0
308 | 0.0033924 | 0.031704 | 0.0011733 | 0.012654 | 0.0011759 | 0.010109 | 0.0033874 | 0.031385 | 0.0011733 | 0.012654 | 0.0033924 | 0.031704 | 0 | 0 | 0 | 0 | 0 | 0 | 0
309 | 0.0010013 | 0.01506 | 0.00060041 | 0.0064753 | 0.00060173 | 0.005173 | 0.00099871 | 0.014896 | 0.00060041 | 0.0064753 | 0.0010013 | 0.01506 | 0 | 0 | 0 | 0 | 0 | 0 | 0
310 | 0.0015778 | 0.023731 | 0.00094614 | 0.010204 | 0.00094823 | 0.0081517 | 0.0015738 | 0.023474 | 0.00094614 | 0.010204 | 0.0015778 | 0.023731 | 0 | 0 | 0 | 0 | 0 | 0 | 0
311 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00014469 | 0.00058252 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
312 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00055417 | 0.002231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
313 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0078341 | 0.031539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0066949 | 0.026953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
315 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00676 | 0.027215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
316 | 0.0014705 | 0.022118 | 0.0008818 | 0.0095101 | 0.00088375 | 0.0075974 | 0.0014668 | 0.021877 | 0.0008818 | 0.0095101 | 0.0014705 | 0.022118 | 0 | 0 | 0 | 0 | 0 | 0 | 0
317 | 0.0014343 | 0.021572 | 0.00086005 | 0.0092755 | 0.00086195 | 0.00741 | 0.0014306 | 0.021338 | 0.00086005 | 0.0092755 | 0.0014343 | 0.021572 | 0 | 0 | 0 | 0 | 0 | 0 | 0
318 | 0.001685 | 0.025343 | 0.0010104 | 0.010897 | 0.0010126 | 0.0087055 | 0.0016807 | 0.025068 | 0.0010104 | 0.010897 | 0.001685 | 0.025343 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | 0.00013142 | 0.00057175 | 3.8129e-05 | 0.00022183 | 3.7989e-05 | 0.00017919 | 0.00013171 | 0.00056669 | 3.8129e-05 | 0.00022183 | 0.00013142 | 0.00057175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
320 | 0.00037586 | 0.0016352 | 0.00010905 | 0.00063444 | 0.00010865 | 0.00051248 | 0.00037668 | 0.0016207 | 0.00010905 | 0.00063444 | 0.00037586 | 0.0016352 | 0 | 0 | 0 | 0 | 0 | 0 | 0
321 | 0.0064015 | 0.02785 | 0.0018573 | 0.010805 | 0.0018504 | 0.0087283 | 0.0064154 | 0.027603 | 0.0018573 | 0.010805 | 0.0064015 | 0.02785 | 0 | 0 | 0 | 0 | 0 | 0 | 0
322 | 0.0016868 | 0.02537 | 0.0010115 | 0.010908 | 0.0010137 | 0.0087145 | 0.0016825 | 0.025094 | 0.0010115 | 0.010908 | 0.0016868 | 0.02537 | 0 | 0 | 0 | 0 | 0 | 0 | 0
323 | 0.0010923 | 0.016429 | 0.00065501 | 0.0070643 | 0.00065646 | 0.0056435 | 0.0010895 | 0.016251 | 0.00065501 | 0.0070643 | 0.0010923 | 0.016429 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | 2.1892e-05 | 0.00017895 | 9.5671e-06 | 7.2926e-05 | 9.5525e-06 | 5.8727e-05 | 2.1922e-05 | 0.00017723 | 9.5671e-06 | 7.2926e-05 | 2.1892e-05 | 0.00017895 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | 0.00010946 | 0.00089474 | 4.7836e-05 | 0.00036463 | 4.7763e-05 | 0.00029364 | 0.00010961 | 0.00088615 | 4.7836e-05 | 0.00036463 | 0.00010946 | 0.00089474 | 0 | 0 | 0 | 0 | 0 | 0 | 0
326 | 0.0016091 | 0.019251 | 0.0011076 | 0.0084427 | 0.0011059 | 0.0067989 | 0.0016126 | 0.019052 | 0.0011076 | 0.0084427 | 0.0016091 | 0.019251 | 0 | 0 | 0 | 0 | 0 | 0 | 0
327 | 5.7165e-05 | 0.00036157 | 1.8925e-05 | 0.00014424 | 1.8896e-05 | 0.00011586 | 5.7226e-05 | 0.0003581 | 1.8925e-05 | 0.00014424 | 5.7165e-05 | 0.00036157 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | 0.0025916 | 0.031005 | 0.0017839 | 0.013598 | 0.0017812 | 0.01095 | 0.0025973 | 0.030685 | 0.0017839 | 0.013598 | 0.0025916 | 0.031005 | 0 | 0 | 0 | 0 | 0 | 0 | 0
329 | 0.0019921 | 0.016284 | 0.00087061 | 0.0066363 | 0.00086928 | 0.0053442 | 0.0019949 | 0.016128 | 0.00087061 | 0.0066363 | 0.0019921 | 0.016284 | 0 | 0 | 0 | 0 | 0 | 0 | 0
330 | 0.004946 | 0.031285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
331 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019913 | 0.00062359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
332 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012744 | 0.003991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
333 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072669 | 0.022757 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
334 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01087 | 0.034042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
335 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099744 | 0.031236 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
336 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095051 | 0.029766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
337 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099419 | 0.031134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
338 | 0.0026791 | 0.0219 | 0.0011708 | 0.0089247 | 0.001169 | 0.0071871 | 0.0026828 | 0.02169 | 0.0011708 | 0.0089247 | 0.0026791 | 0.0219 | 0 | 0 | 0 | 0 | 0 | 0 | 0
339 | 0.002984 | 0.024392 | 0.0013041 | 0.0099406 | 0.0013021 | 0.0080051 | 0.0029882 | 0.024158 | 0.0013041 | 0.0099406 | 0.002984 | 0.024392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
340 | 0.00387 | 0.031634 | 0.0016913 | 0.012892 | 0.0016887 | 0.010382 | 0.0038754 | 0.031331 | 0.0016913 | 0.012892 | 0.00387 | 0.031634 | 0 | 0 | 0 | 0 | 0 | 0 | 0
341 | 0.0028258 | 0.023099 | 0.0012349 | 0.0094133 | 0.001233 | 0.0075805 | 0.0028297 | 0.022877 | 0.0012349 | 0.0094133 | 0.0028258 | 0.023099 | 0 | 0 | 0 | 0 | 0 | 0 | 0
342 | 0.00013142 | 0.00057175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
343 | 0.004782 | 0.020804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
344 | 0.01081 | 0.047028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
345 | 0.0046448 | 0.0020179 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
346 | 0.10246 | 0.044514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
347 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00052836 | 0.0016546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011948 | 0.0037415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052803 | 0.016535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
350 | 0 | 0 | 0 | 0 | 0 | 0 | 0.011143 | 0.034894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012173 | 0.03812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010609 | 0.033223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
353 | 0.0041983 | 0.026555 | 0.001379 | 0.010512 | 0.0013769 | 0.008465 | 0.0042027 | 0.026308 | 0.001379 | 0.010512 | 0.0041983 | 0.026555 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | 0.0038563 | 0.024392 | 0.0012667 | 0.0096555 | 0.0012648 | 0.0077755 | 0.0038604 | 0.024165 | 0.0012667 | 0.0096555 | 0.0038563 | 0.024392 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | 0.0040762 | 0.025783 | 0.0013389 | 0.010206 | 0.0013369 | 0.0082189 | 0.0040805 | 0.025543 | 0.0013389 | 0.010206 | 0.0040762 | 0.025783 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | 0.0040069 | 0.025345 | 0.0013162 | 0.010032 | 0.0013141 | 0.0080791 | 0.0040111 | 0.025109 | 0.0013162 | 0.010032 | 0.0040069 | 0.025345 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | 0.0041374 | 0.02617 | 0.001359 | 0.010359 | 0.0013569 | 0.0083422 | 0.0041417 | 0.025926 | 0.001359 | 0.010359 | 0.0041374 | 0.02617 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | 0.0041651 | 0.026345 | 0.0013681 | 0.010428 | 0.001366 | 0.008398 | 0.0041694 | 0.0261 | 0.0013681 | 0.010428 | 0.0041651 | 0.026345 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | 0.0044788 | 0.02833 | 0.0014711 | 0.011214 | 0.0014689 | 0.0090305 | 0.0044835 | 0.028066 | 0.0014711 | 0.011214 | 0.0044788 | 0.02833 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | 8.7379e-05 | 0.0005527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
361 | 0.00054845 | 0.0034691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
362 | 0.0047622 | 0.030122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
363 | 0.0049856 | 0.031535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
364 | 0.004445 | 0.028116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
365 | 0.0047849 | 0.030266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
366 | 0.0097928 | 0.042802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
367 | 0.0082247 | 0.035948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
368 | 0.0048744 | 0.021305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
369 | 0.0060145 | 0.026288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
370 | 0.0054518 | 0.023718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | 0.0083264 | 0.036224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | 0.0063531 | 0.029595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
373 | 0.0047135 | 0.029814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
374 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00019913 | 0.00062359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
375 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0012147 | 0.0038039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
376 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0075125 | 0.023526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
377 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008844 | 0.027696 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055031 | 0.034448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
379 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0047645 | 0.029825 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
380 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0049421 | 0.030936 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
381 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044216 | 0.027679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
382 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010002 | 0.031323 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
383 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099704 | 0.031223 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
384 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010959 | 0.03432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
385 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097627 | 0.030572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
386 | 0.0033527 | 0.021207 | 0.0011013 | 0.0083946 | 0.0010996 | 0.0067601 | 0.0033563 | 0.021009 | 0.0011013 | 0.0083946 | 0.0033527 | 0.021207 | 0 | 0 | 0 | 0 | 0 | 0 | 0
387 | 0.0046343 | 0.029313 | 0.0015222 | 0.011603 | 0.0015199 | 0.0093441 | 0.0046392 | 0.02904 | 0.0015222 | 0.011603 | 0.0046343 | 0.029313 | 0 | 0 | 0 | 0 | 0 | 0 | 0
388 | 0.0048262 | 0.030527 | 0.0015853 | 0.012084 | 0.0015829 | 0.0097311 | 0.0048313 | 0.030243 | 0.0015853 | 0.012084 | 0.0048262 | 0.030527 | 0 | 0 | 0 | 0 | 0 | 0 | 0
389 | 0.0045932 | 0.029054 | 0.0015087 | 0.0115 | 0.0015064 | 0.0092613 | 0.004598 | 0.028783 | 0.0015087 | 0.0115 | 0.0045932 | 0.029054 | 0 | 0 | 0 | 0 | 0 | 0 | 0
390 | 0.0041823 | 0.026454 | 0.0013737 | 0.010471 | 0.0013716 | 0.0084327 | 0.0041866 | 0.026207 | 0.0013737 | 0.010471 | 0.0041823 | 0.026454 | 0 | 0 | 0 | 0 | 0 | 0 | 0
391 | 0.0056383 | 0.035664 | 0.001852 | 0.014117 | 0.0018492 | 0.011368 | 0.0056442 | 0.035331 | 0.001852 | 0.014117 | 0.0056383 | 0.035664 | 0 | 0 | 0 | 0 | 0 | 0 | 0
392 | 0.004662 | 0.029488 | 0.0015313 | 0.011673 | 0.001529 | 0.0093999 | 0.0046669 | 0.029214 | 0.0015313 | 0.011673 | 0.004662 | 0.029488 | 0 | 0 | 0 | 0 | 0 | 0 | 0
393 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00016033 | 0.00066615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
394 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00026851 | 0.0016979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
395 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052603 | 0.018009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
396 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0093107 | 0.031876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
397 | 0 | 0 | 0 | 0 | 0 | 0 | 0.010297 | 0.035254 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
398 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0089934 | 0.030789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0044137 | 0.015111 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
400 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0088468 | 0.030288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
401 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0040831 | 0.02556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
402 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0041858 | 0.026202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
403 | 0.0041217 | 0.026071 | 0.0013538 | 0.01032 | 0.0013518 | 0.0083105 | 0.004126 | 0.025828 | 0.0013538 | 0.01032 | 0.0041217 | 0.026071 | 0 | 0 | 0 | 0 | 0 | 0 | 0
404 | 0.0063254 | 0.04001 | 0.0020777 | 0.015837 | 0.0020745 | 0.012754 | 0.006332 | 0.039637 | 0.0020777 | 0.015837 | 0.0063254 | 0.04001 | 0 | 0 | 0 | 0 | 0 | 0 | 0
405 | 0.0043058 | 0.027235 | 0.0014143 | 0.010781 | 0.0014122 | 0.0086817 | 0.0043103 | 0.026981 | 0.0014143 | 0.010781 | 0.0043058 | 0.027235 | 0 | 0 | 0 | 0 | 0 | 0 | 0
406 | 0.0072245 | 0.045697 | 0.002373 | 0.018089 | 0.0023694 | 0.014567 | 0.0072321 | 0.045271 | 0.002373 | 0.018089 | 0.0072245 | 0.045697 | 0 | 0 | 0 | 0 | 0 | 0 | 0
407 | 0.0082486 | 0.052175 | 0.0027094 | 0.020653 | 0.0027053 | 0.016632 | 0.0082572 | 0.051689 | 0.0027094 | 0.020653 | 0.0082486 | 0.052175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
408 | 0.0083523 | 0.052831 | 0.0027435 | 0.020912 | 0.0027393 | 0.016841 | 0.008361 | 0.052338 | 0.0027435 | 0.020912 | 0.0083523 | 0.052831 | 0 | 0 | 0 | 0 | 0 | 0 | 0
409 | 0.0073148 | 0.046268 | 0.0024027 | 0.018315 | 0.002399 | 0.014749 | 0.0073225 | 0.045837 | 0.0024027 | 0.018315 | 0.0073148 | 0.046268 | 0 | 0 | 0 | 0 | 0 | 0 | 0
410 | 0.0083185 | 0.052617 | 0.0027324 | 0.020828 | 0.0027282 | 0.016773 | 0.0083272 | 0.052127 | 0.0027324 | 0.020828 | 0.0083185 | 0.052617 | 0 | 0 | 0 | 0 | 0 | 0 | 0
411 | 0.008426 | 0.053297 | 0.0027677 | 0.021097 | 0.0027635 | 0.016989 | 0.0084348 | 0.0528 | 0.0027677 | 0.021097 | 0.008426 | 0.053297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
412 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
413 | 0.075142 | 0.023483 | 0.019177 | 0.0019433 | 0.019177 | 0.0019433 | 0.075142 | 0.023483 | 0.019177 | 0.0019433 | 0.075142 | 0.023483 | 0 | 0 | 0 | 0 | 0 | 0 | 0
414 | 0.046269 | 0.012657 | 0.011837 | 0.0010742 | 0.011837 | 0.0010742 | 0.046269 | 0.012657 | 0.011837 | 0.0010742 | 0.046269 | 0.012657 | 0 | 0 | 0 | 0 | 0 | 0 | 0
415 | 0.0036309 | 0.022966 | 0.0011926 | 0.009091 | 0.0011908 | 0.007321 | 0.0036347 | 0.022752 | 0.0011926 | 0.009091 | 0.0036309 | 0.022966 | 0 | 0 | 0 | 0 | 0 | 0 | 0
416 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0.00014264 | 1.4455e-05 | 0.00055892 | 0.00017467 | 0 | 0 | 0 | 0 | 0 | 0 | 0
417 | 0.062836 | 0.019637 | 0.016036 | 0.0016251 | 0.016036 | 0.0016251 | 0.062836 | 0.019637 | 0.016036 | 0.0016251 | 0.062836 | 0.019637 | 0 | 0 | 0 | 0 | 0 | 0 | 0
418 | 0.047695 | 0.014905 | 0.012172 | 0.0012335 | 0.012172 | 0.0012335 | 0.047695 | 0.014905 | 0.012172 | 0.0012335 | 0.047695 | 0.014905 | 0 | 0 | 0 | 0 | 0 | 0 | 0
419 | 0.015927 | 0.0096694 | 0.011897 | 0.0023111 | 0.011897 | 0.0023111 | 0.015927 | 0.0096694 | 0.011897 | 0.0023111 | 0.015927 | 0.0096694 | 0 | 0 | 0 | 0 | 0 | 0 | 0
420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00013142 | 0.00057175 | 0 | 0 | 0 | 0 | 0 | 0 | 0
421 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0065509 | 0.0285 | 0 | 0 | 0 | 0 | 0 | 0 | 0
422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00021903 | 0.00095291 | 0 | 0 | 0 | 0 | 0 | 0 | 0
500 | 0.0922 | 0.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
501 | 0.493 | 0.2511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
502 | 0.164 | 0.1565 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
503 | 0.366 | 0.1864 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
504 | 0.4512 | 0.3083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
505 | 0.3811 | 0.1941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
506 | 0.819 | 0.707 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
507 | 0.1872 | 0.6188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
508 | 0.203 | 0.1034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
509 | 0.7114 | 0.2351 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
510 | 1.03 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
511 | 1.044 | 0.74 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
512 | 0.1966 | 0.065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
513 | 0.3744 | 0.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
514 | 1.468 | 1.155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
515 | 0.5416 | 0.7129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
516 | 0.591 | 0.526 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
517 | 0.7463 | 0.545 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
518 | 1.289 | 1.721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
519 | 0.732 | 0.574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
520 | 1.5042 | 1.3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
521 | 0.4095 | 0.4784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
522 | 0.7089 | 0.9373 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
523 | 0.898 | 0.7091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
524 | 0.896 | 0.7011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
525 | 0.2842 | 0.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
526 | 1.059 | 0.9337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
527 | 0.8042 | 0.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
528 | 0.5075 | 0.2585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
529 | 0.9744 | 0.963 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
530 | 0.3105 | 0.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
531 | 0.341 | 0.5302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
532 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
533 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
534 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
535 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
536 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
537 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
538 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
539 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
540 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
541 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
542 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
543 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
544 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
545 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
546 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
547 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
548 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
549 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
550 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
551 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
552 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
553 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
554 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
555 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
556 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
557 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
558 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
559 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
560 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
561 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
562 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
563 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
564 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
565 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
566 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
567 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
568 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
569 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
570 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
571 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
572 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
573 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
574 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
575 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
576 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
577 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
578 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
579 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
580 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
581 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
582 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
583 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
584 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
585 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
586 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
587 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
588 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
589 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
590 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
591 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
592 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
593 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
594 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
595 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
596 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
597 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
598 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
599 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
600 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
601 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
602 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
603 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
604 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
605 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
606 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
607 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
608 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
609 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
610 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
611 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
612 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
613 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
614 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
615 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
616 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
617 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
618 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
619 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
620 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
621 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
622 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
623 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
624 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
625 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
626 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
627 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
628 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
629 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
630 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
631 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
632 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
633 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
634 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
635 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
636 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
637 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
638 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
639 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
640 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
641 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
642 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
643 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
644 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
645 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
646 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
647 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
648 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
649 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
650 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
651 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
652 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
653 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
654 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
655 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
656 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
657 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
658 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
659 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
660 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
661 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
662 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
663 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
664 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
665 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
666 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
667 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
668 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
669 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
670 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
671 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
672 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
673 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
674 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
675 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
676 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
677 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
678 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
679 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
680 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
681 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
682 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
683 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
684 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
685 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
686 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
687 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
688 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
689 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
690 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
691 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
692 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
693 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
694 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
695 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
696 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
697 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
698 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
699 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
700 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
701 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
702 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
703 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
704 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
705 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
706 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
707 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
708 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
709 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
710 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
711 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
712 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
713 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
714 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
715 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
716 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
717 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
718 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
719 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
720 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
721 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
722 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
723 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
724 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
725 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
726 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
727 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
728 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
729 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
730 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
731 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
732 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
733 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
734 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
735 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
736 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
737 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
738 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
739 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
740 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
741 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
742 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
743 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
744 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
745 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
746 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
747 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
748 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
749 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
750 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
751 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
752 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
753 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
754 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
755 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
756 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
757 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
758 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
759 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
760 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
761 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
762 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
763 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
764 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
765 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
766 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
767 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
768 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
769 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
770 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
771 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
772 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
773 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
774 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
775 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
776 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
777 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
778 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
779 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
780 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
781 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
782 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
783 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
784 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
785 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
786 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
787 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
788 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
789 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
790 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
791 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
792 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
793 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
794 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
795 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
796 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
797 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
798 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
799 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
800 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
801 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
802 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
803 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
804 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
805 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
806 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
807 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
808 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
809 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
810 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
811 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
812 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
813 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
814 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
815 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
816 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
817 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
818 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
819 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
820 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
821 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
822 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
823 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
824 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
825 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
826 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
827 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
828 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
829 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
830 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
831 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
832 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
833 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
834 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
835 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
836 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
837 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
838 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
839 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
840 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
841 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
842 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
843 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
844 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
845 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
846 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
847 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
848 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
849 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
850 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
851 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
852 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
853 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
854 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
855 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
856 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
857 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
858 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
859 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
860 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
861 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
862 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
863 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
864 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
865 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
866 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
867 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
868 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
869 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
870 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
871 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
872 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
873 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
874 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
875 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
876 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
877 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
878 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
879 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
880 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
881 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
882 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
883 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
884 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
885 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
886 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
887 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
888 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
889 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
890 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
891 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
892 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
893 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
894 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
895 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
896 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
897 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
898 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
899 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
900 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
901 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
902 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
903 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
904 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
905 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
906 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
907 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
908 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
909 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
910 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
911 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
912 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
913 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
914 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
915 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
916 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
917 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
918 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
919 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
920 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
921 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
922 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
923 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
924 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
925 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
926 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
927 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
928 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
929 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
930 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
931 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
932 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
933 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
934 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
935 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
936 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
937 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
938 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
939 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
940 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
941 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
942 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
943 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
944 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
945 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
946 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
947 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
948 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
949 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
950 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
951 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
952 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
953 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
954 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
955 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
956 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
957 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
958 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
959 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
960 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
961 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
962 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
963 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
964 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
965 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
966 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
967 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
968 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
969 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
970 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
971 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
972 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
973 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
974 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
975 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
976 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
977 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
978 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
979 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
980 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
981 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
982 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
983 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
984 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
985 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
986 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
987 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
988 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
989 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
990 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
991 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
992 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
993 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
994 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
995 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
996 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
997 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
998 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
999 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1000 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1001 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1002 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1003 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1004 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1005 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1006 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1007 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1008 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1009 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1010 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1011 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1012 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1013 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1014 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1015 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1016 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1017 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1018 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1019 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1020 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1021 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1022 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1023 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1024 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1025 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1026 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1027 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1028 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1029 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1030 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1031 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1032 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1033 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1034 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1035 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1036 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1037 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1038 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1039 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1040 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1041 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1042 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1043 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1044 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1045 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1046 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1047 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1048 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1049 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1050 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1051 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1052 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1053 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1054 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1055 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1056 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1057 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1058 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1059 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1060 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1061 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1062 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1063 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1064 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1065 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1066 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1067 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1068 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1069 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1070 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1071 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1072 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1073 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1074 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1075 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1076 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1077 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1078 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1079 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1080 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1081 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1082 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1083 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1084 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1085 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1086 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1087 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1088 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1089 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1090 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1091 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1092 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1093 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1094 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1095 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1096 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1097 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1098 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1099 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1100 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1101 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1102 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1103 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1104 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1105 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1106 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1107 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1108 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1109 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1110 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1111 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1112 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1113 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1114 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1115 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1116 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1117 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1118 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1119 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1120 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1121 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1122 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1123 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1124 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1125 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1126 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1127 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1128 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1129 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1130 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1131 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1132 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1133 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1134 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1135 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1136 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1137 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1138 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1139 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1140 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1141 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1142 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1143 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1144 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1145 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1146 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1147 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1148 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1149 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1150 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1151 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1152 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1153 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1154 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1155 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1156 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1157 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1158 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1159 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1160 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1161 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1162 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1163 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1164 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1165 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1166 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1167 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1168 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1169 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1170 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1171 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1172 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1173 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1174 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1175 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1176 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1177 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1178 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1179 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1180 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1181 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1182 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1183 | 0.0069 | 0.0018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1184 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1185 | 0.011 | 0.0017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Configuration
No | Config | Phasing | Cable | SpacingID | PhA_ cond | PhB_ cond | PhC_ cond | Neu_Cond | Type | n | Outside diameter (Dod) | No of strands(k) (cable only!) | Relative permittivity (Cable!) | 1_flag | 2_flag | 3_flag | Neu_Flag_1 | Neu_Flag_2 | Neu_Flag_3 | dis Cable and neutral
1 | 1 | BACN | 601 | 1 | 2 | 2 | 2 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
2 | 2 | C A B N | 602 | 2 | 6 | 6 | 6 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
3 | 3 | CBN | 603 | 3 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 0 | 1 | 1 | 1 | 0 | 0
4 | 4 | CAN | 604 | 4 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 1 | 0 | 1 | 1 | 0 | 0
5 | 5 | CN | 605 | 5 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 0 | 0 | 1 | 1 | 0 | 0
6 | 6 | ABCN UG | 606 | 6 | 4 | 4 | 4 | 15 | 1 | 6 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 1 | 1
7 | 7 | AN UG TS | 607 | - | 16 | - | - | 9 | 2 | 3 | 0.88 | 5 |  | 1 | 0 | 0 | 1 | 0 | 0 | 0.08333
8 | 8 | ABCN UG | 721 | 6 | 1 | 1 | 1 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
9 | 9 | ABCN UG | 722 | 6 | 3 | 3 | 3 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
10 | 10 | ABCN UG | 723 | 6 | 7 | 7 | 7 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
11 | 11 | ABCN UG | 724 | 6 | 10 | 10 | 10 | 14 | 1 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
12 | 12 | BACN | 300 | 1 | 8 | 8 | 8 | 8 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
13 | 13 | BACN | 301 | 1 | 11 | 11 | 11 | 11 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
14 | 14 | AN OH | 302 | 8 | 12 | 12 | 12 | 12 | 0 | 3 | 1.29 | 13 |  | 1 | 0 | 0 | 1 | 0 | 0
15 | 15 | BN OH | 303 | 9 | 12 | 12 | 12 | 12 | 0 | 3 | 1.29 | 13 |  | 0 | 1 | 0 | 1 | 0 | 0
16 | 16 | BN OH | 304 | 9 | 11 | 11 | 11 | 11 | 0 | 3 | 1.29 | 13 |  | 0 | 1 | 0 | 1 | 0 | 0
17 | 17 | ABC N OHL | 708 | 10 | 5 | 5 | 5 | 6 | 0 | 4 | 1.29 | 13 |  | 1 | 1 | 1 | 1 | 0 | 0
18 | 18 | ABC N OHL | 708 | 11 | 5 | 5 | 5 | 6 | 0 | 3 | 1.29 | 13 |  | 1 | 1 | 1 | 0 | 0 | 0
Note on J1: Author: 0 - OH Lines 1 - Concentric Neutral Cable 2 - Tape Shielded Cable
Note on K1: Author: Primitive size of Matrix

## Conductortype
No | Conductor | Type | Res. (Ohms/mi) | Dia. (Inch) | GMR (Ft) | Rating (Amps)
1 | 1,000,000 CM | AA | 0.105 | 1.15 | 0.0368 | 698
2 | 556,500 CM | ACSR | 0.186 | 0.927 | 0.0311 | 730
3 | 500,000 CM | AA | 0.206 | 0.813 | 0.026 | 483
4 | 250,000 CM | AA | 0.41 | 0.567 | 0.0171 | 329
5 | 336,400 CM | ACSR | 0.306 | 0.721 | 0.0244 | 530
6 | #4/0 | ACSR | 0.592 | 0.563 | 0.00814 | 340
7 | #2/0 | AA | 0.769 | 0.414 | 0.0125 | 230
8 | #1/0 | ACSR | 1.12 | 0.398 | 0.00446 | 230
9 | #1/0 | CU | 0.607 | 0.368 | 0.01113 | 310
10 | #2 | AA | 1.54 | 0.292 | 0.00883 | 156
11 | #2 | ACSR | 1.69 | 0.316 | 0.00418 | 180
12 | #4 | ACSR | 2.55 | 0.257 | 0.00452 | 140
13 | #10 | CU | 5.903 | 0.102 | 0.00331 | 80
14 | #12 | CU | 9.375 | 0.081 | 0.00262 | 75
15 | #14 | CU | 14.872 | 0.064 | 0.00208 | 20
16 | #1/0 | AA | 0.97 | 0.368 | 0.0111 | 202
17 | #4 | ACSR | 2.57 | 0.25 | 0.00437 | 140

## Spacing
SI No | Spacing No | n | X-PhaseCond1 | Y-PhaseCond2 | X-PhaseCond2 | Y-PhaseCond2 | X-PhaseCond3 | Y-PhaseCond3 | X-Neutral1 | Y-Neutral1 | X-Neutral2 | Y-Neutral2 | X-Neutral3 | Y-Neutral3
1 | 1 | 4 | 2.5 | 28 | 0 | 28 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
2 | 2 | 4 | 2.5 | 28 | 7 | 28 | 0 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
3 | 3 | 4 | 9999 | 9999 | 7 | 28 | 0 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
4 | 4 | 4 | 0 | 28 | 9999 | 9999 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
5 | 5 | 4 | 9999 | 9999 | 9999 | 9999 | 0 | 29 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
6 | 6 | 6 | 0 | 0 | 0.5 | 0 | 1 | 0 | 0 | 0.0511 | 0.5 | 0.0511 | 1 | 0.0511 | 515
7 | 7 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 9999 | 9999 | 9999 | 9999
8 | 8 | 4 | 0 | 29 | 9999 | 9999 | 9999 | 9999 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
9 | 9 | 4 | 9999 | 9999 | 0 | 29 | 9999 | 9999 | 0.5 | 24 | 9999 | 9999 | 9999 | 9999
10 | 10 | 4 | 0 | 28 | 2.5 | 28 | 7 | 28 | 4 | 24 | 9999 | 9999 | 9999 | 9999
11 | 11 | 4 | 0 | 28 | 2.5 | 28 | 7 | 28 | 9999 | 9999 | 9999 | 9999 | 9999 | 9999